IEEE 2030.7 / 2030.8 Compliance Gap Analysis (East Coast)

1. IEEE 2030.7 / 2030.8 – Standard Baseline Review

1.1 Functional Architecture (2030.7)

IEEE 2030.7 defines the Microgrid Energy Management System (MEMS) as the central controller responsible for system-level coordination across DERs, loads, and grid interface. [ 2030.7-2017 - IEEE Standard for the Specification of Microgrid Controllers | IEEE Standard | IEEE Xplore]

Core functional layers

| Function Layer | Description | Key Requirements |
| --- | --- | --- |
| Dispatch Function | Determines optimal DER output based on load, cost, constraints | Economic dispatch, load prioritization |
| Transition Function | Controls islanding / reconnection | Seamless grid ↔ island switching |
| Protection Coordination | Ensures safe operation under faults/abnormal conditions | Coordination with utility protection |
| EMS Optimization | Forecasting + optimization | Load, PV, storage scheduling |
| Communication | Controller-to-device and utility interface | Interoperability |

The standard emphasizes autonomous operation, grid-connected + islanded capability, and ancillary service participation

1.2 Operational Modes

| Mode | Core Requirement |
| --- | --- |
| Grid-connected Islanded Transition Emergency | Economic dispatch Load prioritization Smooth synchronization Critical load survival |

1.3 IEEE 2030.8 – Testing Standard

IEEE 2030.8 defines test procedures to validate controller performance. [ https://ieeexplore.ieee.org/document/8444947]

Test categories

| Test Type | Examples |
| --- | --- |
| Functional tests | Dispatch accuracy, load balance |
| Dynamic tests | Frequency/voltage disturbance |
| Transition tests | Islanding/reconnection |
| Resilience tests | Black start, fault recovery |

Key Insight

2030.7 = Functional specification
2030.8 = Validation & certification pathway

2. Regional Interconnection Rules Mapping

2.1 Core Standard: IEEE 1547-2018

IEEE 1547 defines DER interconnection requirements including:

- Voltage regulation

- Frequency ride-through

- Grid support functions

- Testing/commissioning requirements [ https://ieeexplore.ieee.org/document/8332112]

2.2 East Coast RTO Mapping

| Region | Governing Body | Key Documents | DER Focus |
| --- | --- | --- | --- |
| PJM | PJM Interconnection | Manual 14G, Tech Requirements | Market-based DER participation |
| NYISO | NYSERDA + NY PSC | SIR + VDER | Advanced DER + value stack |
| ISO-NE | ISO New England | Interconnection Procedures | Strict protection/control |
| MISO (East) | MISO | Generator Interconnection Queue | Transmission-level compliance |
| SERC | NERC regional entity | Reliability standards | Protection + stability |

2.3 IEEE 1547 Adoption

- Most East Coast states mandate or are transitioning to 1547-2018

- Smart inverter compliance (UL 1741 SB) widely required
[ https://irecusa.org/resources/ieee-1547-2018-adoption-tracker/]

2.4 PJM Example Requirements

- DER must align with IEEE 1547 definitions and performance [ https://www.pjm.com/-/media/DotCom/planning/plan-standards/private-fe/technical-interconnection-requirement-der-interconnect-to-distribution-systems.pdf]

- Must support:

  - Ride-through

  - Voltage/frequency control

  - Protection coordination

Gap vs Delta

| Area | Requirement | Gap Risk |
| --- | --- | --- |
| Smart inverter | Mandatory grid support functions | Medium |
| Market integration | PJM participation readiness | High |
| Ride-through compliance | Certification required | Medium |

3. Utility-Specific Microgrid Requirements

3.1 Con Edison (Reference Utility)

ConEd microgrid specification focuses on:

- Safe interconnection with EPS

- Network grid operation constraints

- Protection coordination

- Operational modes across feeder types [ https://www.coned.com/-/media/files/coned/documents/save-energy-money/using-private-generation/specs-and-tariffs/eo-2161.pdf?la=en]

3.2 Common Utility Requirements (Aggregated)

| Utility | Key Requirements |
| --- | --- |
| ConEd | Network grid compatibility, protection coordination |
| Eversource | DER visibility + SCADA integration |
| Duke Energy | Grid support + voltage regulation |
| Dominion | Protection + islanding control |
| DTE / ComEd | Advanced metering + telemetry |

3.3 Functional Overlay vs IEEE 2030.7

| Function | IEEE 2030.7 | U.S. Utilities |
| --- | --- | --- |
| Dispatch | Required | Required + market linkage |
| Transition | Required | Strict switching requirements |
| Protection | High-level | Highly specific schemes |
| SCADA | General | Mandatory integration |

4. Test Framework Gap Analysis (Delta vs 2030.8)

Delta Current (Taipower-based)

Typical features:

- Grid-following inverter validation

- Static performance tests

- Limited dynamic ride-through

2030.8 Requirements

| Category | Required |
| --- | --- |
| Dynamic simulation | Mandatory |
| HIL testing | Preferred |
| Transition testing | Mandatory |
| Failure scenarios | Extensive |

Gap Matrix

| Area | Delta | 2030.8 Requirement | Gap |
| --- | --- | --- | --- |
| Transition testing | Limited | Full test suite | HIGH |
| Black start | Likely absent | Required | HIGH |
| HIL validation | Partial | Recommended | MEDIUM |
| Dynamic DER coordination | Limited | Required | HIGH |

5. Certification & Lab Pathway

Relevant Labs

| Lab | Location | Scope |
| --- | --- | --- |
| Intertek | NJ, TX | UL / grid testing |
| KEMA (CESI) | Global | Type test certification |
| PowerCert / NRTL | US | DER validation |

Typical Timeline

| Phase | Duration |
| --- | --- |
| Pre-validation | 3–6 months |
| Lab certification | 6–12 months |
| Utility approval | 3–9 months |

6. Consolidated Gap Summary

Technical Gaps

| Area | Severity |
| --- | --- |
| Transition functionality | HIGH |
| Protection coordination | HIGH |
| Market integration (PJM/NYISO) | HIGH |
| 2030.8 testing coverage | HIGH |
| SCADA interoperability | MEDIUM |

Business Risks

- Utility rejection due to non-standard protection

- Failure to meet IEEE 1547 + UL certification

- Delays in interconnection approval

Recommendations

- Develop 2030.8-compliant test suite

- Add market participation module (PJM/NYISO)

- Integrate IEC 61850 / DNP3 SCADA

- Build utility-specific controller profiles

S-UI-03: Utility Metering & CT/PT Specification Package

1. Standards Overview

1.1 ANSI Meter Standards

| Standard | Description | Accuracy |
| --- | --- | --- |
| ANSI C12.1 | General performance | ~1% |
| ANSI C12.20 | High accuracy | 0.2 / 0.5 class |

[https://powerquality.blog/2026/01/08/revenue-accurate-vs-revenue-certified-grade/]

1.2 CT/PT Standards

| Standard | Description |
| --- | --- |
| IEEE C57.13 | Instrument transformers |
| IEC 61869 | Global equivalent |

1.3 Accuracy Classes

| Class | Usage |
| --- | --- |
| 0.2S | Revenue-grade utility |
| 0.5S | Commercial billing |
| 1.0 | Monitoring only |

2. Metering Requirements (East Coast)

Regional Characteristics

| Region | Billing Type |
| --- | --- |
| NYISO | Value Stack (VDER) |
| PJM | Capacity + energy |
| ISO-NE | Forward capacity market |
| MISO | Wholesale settlement |

Utility Trends

- Mandatory interval metering (5–15 min)

- Revenue-grade accuracy required

- SCADA + AMI integration

3. Utility Metering Requirements

| Utility | Meter Requirement |
| --- | --- |
| ConEd | Revenue-grade + VDER |
| Eversource | AMI + remote telemetry |
| Duke | TOU + demand billing |
| DTE | SCADA-integrated meters |

4. CT/PT Selection Matrix (MV 15–35 kV)

CT Selection

| Parameter | Typical Value |
| --- | --- |
| Ratio | 200:5 – 2000:5 |
| Accuracy | 0.15 / 0.3 |
| Burden | B-0.1 to B-1.8 |

PT Selection

| Parameter | Typical Value |
| --- | --- |
| Voltage | 15–35 kV |
| Accuracy | 0.15 / 0.3 |
| Burden | 25–100 VA |

Selection Table

| Application | CT Class | PT Class |
| --- | --- | --- |
| Utility billing | 0.15 | 0.15 |
| Commercial | 0.3 | 0.3 |
| Monitoring | 0.6 | 0.6 |

Revenue metering requires ±0.15–0.3% accuracy and stable burden handling. [ https://duomatech.com/pt-selection-metering-revenue-applications-accuracy-burden-compliance/]

5. Communications & SCADA Architecture

Protocols

| Protocol | Use |
| --- | --- |
| DNP3 | Utility SCADA |
| Modbus | Local control |
| IEC 61850 | Substation integration |

Architecture Diagram

[Meter] → [RTU] → [Utility SCADA] → [EMS / Microgrid Controller]

6. Vendor Benchmarking

| Vendor | Strength |
| --- | --- |
| Itron | Utility-grade AMI |
| Landis+Gyr | Smart metering leader |
| Schneider | Integrated systems |
| GE Vernova | Grid-scale solutions |

7. Delta Metering Specification

Core Requirements

- ANSI C12.20 Class 0.2 meter

- CT/PT accuracy 0.15 class

- IEC 61850 + DNP3 support

- Interval data (≤5 min)

- Cybersecure communication

Functional Requirements

| Category | Requirement |
| --- | --- |
| Billing | TOU + net metering |
| Data | Revenue-grade logging |
| Integration | SCADA + EMS |
| Cybersecurity | NERC CIP alignment |

8. Revenue Leakage Checklist

Correct CT/PT ratio
Phase angle compensation
Time sync (GPS)
Calibration schedule
Tamper detection
Loss compensation

Final Executive Summary

Key Findings

- IEEE 2030.7 provides architecture, but utilities demand implementation detail

- IEEE 2030.8 compliance is major gap area for Delta

- East Coast utilities require strict SCADA + protection integration

- Revenue metering requires high-precision CT/PT + ANSI compliance

Critical Gaps

- Lack of full 2030.8 test compliance

- Missing utility-specific protection schemes

- Limited market integration capability

- Incomplete revenue metering specification alignment

Strategic Recommendations

Short-Term

- Align controller with IEEE 2030.7 functions

- Build 2030.8 test framework

Mid-Term

- Engage Intertek/KEMA for certification

- Develop utility-specific configurations

Long-Term

- Position Delta as:

  - Certified microgrid integrator

  - Utility-grade metering solution provider