PSCAD v5.0.2 Step-by-Step Procedure for PCS3440 MV Inverter Model

Below is a practical modeling procedure for implementing a PCS3440 medium-voltage inverter model in PSCAD v5.0.2 with:

- Grid-following control

- Grid-forming control

- Current saturation and fault behavior

- Integrated MV transformer model

- Unit controller logic

- Microgrid controller logic

This is written as an engineering implementation guide. Exact manufacturer parameters for the PCS3440 should be used where available. Where not available, typical values are provided.

1. Overall PSCAD Model Architecture

The PCS3440 MV inverter model can be divided into the following building blocks:

Main PSCAD Subsystems

- DC source / DC link

- Three-phase inverter bridge

- LCL or LC filter

- 690 V inverter-side AC bus

- 690 V / 13.2 kV MV transformer

- 13.2 kV grid or microgrid bus

- Measurement block

- Grid-following controller

- Grid-forming controller

- Current limiter / saturation block

- Mode transition logic

- Unit controller

- Microgrid controller

A simplified signal flow is:

Grid / PCC Measurements

|

v

PLL / Frequency Estimator

|

v

Power, Voltage, Current Calculations

|

+----------------------------+

|                            |

v                            v

Grid-Following Controller      Grid-Forming Controller

|                            |

+------------ Mode Selector -+

|

v

Current Limiter

|

v

PWM / Switching Model

|

v

Inverter + Filter

|

v

Transformer + Grid

Part A — Base Electrical Model

2. Define System Base Values

Assume PCS3440 is approximately:

| Quantity | Value |
| --- | --- |
| Rated apparent power | 3440 kVA |
| Low-voltage side | 690 V LL RMS |
| MV side | 13.2 kV LL RMS |
| Transformer rating | 3000 kVA |
| Frequency | 60 Hz |
| DC-link voltage | Depends on inverter design |

You should define base quantities on both LV and MV sides.

Three-phase base current

Ibase​=3​VLL,base​Sbase​​

For 3440 kVA at 690 V:

Ibase,LV​=3​×6903.44×106​ Ibase,LV​≈2879 A

For 3440 kVA at 13.2 kV:

Ibase,MV​=3​×132003.44×106​ Ibase,MV​≈150.5 A

3. Inverter Power Stage Model

In PSCAD, you can model the inverter in two ways:

Option 1 — Detailed switching model

Use:

- IGBT / ideal switch bridge

- PWM generator

- Carrier frequency, e.g. 2–5 kHz

- DC-link capacitor

- Snubber or numerical damping if needed

This is useful for:

- Harmonics

- Switching studies

- Filter design

- EMT transient analysis

Option 2 — Average-value inverter model

Use controlled voltage sources in the abc frame.

This is useful for:

- Control design

- Grid-forming / grid-following studies

- Stability analysis

- Weak-grid behavior

- Faster simulation

For most PSCAD control studies, start with an average-value model first.

The inverter voltage command is:

vabc∗​=Tdq0−1​vdq∗​

where the inverse Park transform converts dq commands into three-phase voltage commands.

4. L Filter or LCL Filter

For the current controller, a simplified L filter is commonly used.

The dq filter equations are:

vinv,d​=vgrid,d​+Rf​id​+Lf​dtdid​​−ωLf​iq​ vinv,q​=vgrid,q​+Rf​iq​+Lf​dtdiq​​+ωLf​id​

Where:

| Symbol | Meaning |
| --- | --- |
| vinv,dq​ | inverter voltage command |
| vgrid,dq​ | measured PCC voltage |
| Rf​ | filter resistance |
| Lf​ | filter inductance |
| idq​ | inverter current |
| ω | synchronous angular frequency |

A typical filter impedance is 5–15% pu.

Part B — Grid-Following Control Mode

5. SRF-PLL With Bandwidth Tuning

The synchronous reference frame PLL aligns the d-axis or q-axis with the grid voltage.

A common convention is:

vq​→0

The PLL controller is:

ωPLL​=ω0​+Kp,PLL​vq​+Ki,PLL​∫vq​dt θPLL​=∫ωPLL​dt

For normalized voltage, PLL PI gains can be tuned as:

Kp,PLL​=2ζωBW​ Ki,PLL​=ωBW2​

where:

ωBW​=2πfBW​

Typical damping:

ζ=0.707

For PLL bandwidth from 10 Hz to 50 Hz:

| PLL Bandwidth | ωBW​ | Kp​ | Ki​ |
| --- | --- | --- | --- |
| 10 Hz | 62.83 rad/s | 88.8 | 3948 |
| 20 Hz | 125.66 rad/s | 177.7 | 15791 |
| 50 Hz | 314.16 rad/s | 444.3 | 98696 |

Weak-grid stability recommendation

For weak grids, especially SCR below 3:

- Use PLL bandwidth closer to 10–20 Hz.

- Avoid 50 Hz PLL bandwidth unless grid is strong.

- Add voltage feedforward filtering.

- Use current-loop bandwidth much higher than PLL bandwidth.

- Check phase margin using impedance scan or small-signal analysis.

A good design rule:

fPLL​<51​fcurrent−loop​

If the current loop bandwidth is 200–300 Hz, use PLL bandwidth less than 40–60 Hz.

For weak grids, prefer:

fPLL​=10 to 20 Hz

6. dq Current Controller

The dq current controller regulates id​ and iq​.

In grid-following mode:

- id​ usually controls active power.

- iq​ usually controls reactive power or voltage support.

The current control equations are:

vd∗​=vpcc,d​+Kp,i​(id∗​−id​)+Ki,i​∫(id∗​−id​)dt−ωLf​iq​ vq∗​=vpcc,q​+Kp,i​(iq∗​−iq​)+Ki,i​∫(iq∗​−iq​)dt+ωLf​id​

Where the cross-coupling terms are:

−ωLf​iq​

and

+ωLf​id​

These improve dynamic response.

7. Current Controller Tuning for Less Than 5 ms Response

For an L-filter plant:

G(s)=Lf​s+Rf​1​

A PI controller:

Gc​(s)=Kp​+sKi​​

A common tuning is:

Kp,i​=Lf​ωci​ Ki,i​=Rf​ωci​

where ωci​ is the desired current loop bandwidth.

For a response time less than 5 ms, choose a closed-loop bandwidth roughly:

fci​=200 to 500 Hz

A practical choice:

fci​=300 Hz ωci​=2π×300=1885 rad/s

Therefore:

Kp,i​=Lf​×1885 Ki,i​=Rf​×1885

If using per-unit control and filter impedance Xf​ is known:

Lf​=ω0​Xf​Zbase​​

where:

Zbase​=Sbase​VLL,base2​​

8. Active Power Control With Ramp-Rate Limiter

Active power is calculated as:

P=23​(vd​id​+vq​iq​)

If PLL aligns the d-axis with voltage, then:

vq​≈0

So:

P≈23​vd​id​

The active current reference is:

id∗​=32​vd​P∗​

Add a ramp limiter to the active power command:

Pcmd​(t)=RampLimit(Pset​,RP​)

where RP​ is in MW/s.

Discrete implementation:

ΔPmax​=RP​Δt Pcmd​[k]=Pcmd​[k−1]+sat(Pset​−Pcmd​[k−1],−ΔPmax​,ΔPmax​)

Example:

If ramp rate is 1 MW/s and PSCAD control time step is 50 µs:

ΔPmax​=1×106×50×10−6=50 W/sample

9. Reactive Power Control

Reactive power is:

Q=23​(vq​id​−vd​iq​)

With vq​≈0:

Q≈−23​vd​iq​

So:

iq∗​=−32​vd​Q∗​

The sign convention depends on PSCAD measurement convention. You should verify whether positive iq​ injects or absorbs reactive power.

10. Power Factor Mode

If operating in power factor mode:

Q∗=P∗tan(cos−1(PF))

For lagging or leading power factor, assign sign based on grid-code convention.

Example:

Lagging PF: inverter supplies positive reactive power

Leading PF: inverter absorbs reactive power

Then:

iq∗​=−32​vd​Q∗​

11. Negative Sequence Current Control

For unbalanced grid conditions, use positive and negative sequence extraction.

The three-phase voltage and current are separated into:

- Positive sequence: vdq+​, idq+​

- Negative sequence: vdq−​, idq−​

Use two rotating reference frames:

Positive sequence frame:

θ+=θPLL​

Negative sequence frame:

θ−=−θPLL​

Positive-sequence current controller:

id+∗​,iq+∗​

Negative-sequence current controller:

id−∗​,iq−∗​

A common grid-code behavior is to inject negative-sequence current proportional to negative-sequence voltage:

iq−∗​=Kneg​vq−​

or:

id−∗​=Kneg​vd−​

depending on required support function.

Current magnitude must remain limited:

(id+​)2+(iq+​)2+(id−​)2+(iq−​)2​≤Imax​

Part C — Grid-Forming Control Mode

12. Grid-Forming Control Overview

In grid-forming mode, the inverter behaves like a controlled voltage source behind an impedance.

Instead of following grid voltage angle from a PLL, the inverter internally generates its own:

- Voltage magnitude

- Frequency

- Phase angle

The main control structure is:

P, Q Measurement

|

v

Droop / VSM Controller

|

v

Frequency and Voltage Reference

|

v

Virtual Impedance

|

v

Voltage Controller

|

v

Current Controller / Modulator

13. P-f Droop Control

Active power-frequency droop is:

ω∗=ω0​−mp​(P−P0​)

or in frequency form:

f∗=f0​−mf​(P−P0​)

For 5% droop, the inverter frequency drops from 60 Hz to 57 Hz at full active power output.

Therefore:

Δf=0.05×60=3 Hz

For rated power Prated​:

mf​=Prated​Δf​

For Prated​=3.44 MW:

mf​=3.443​=0.872 Hz/MW

In rad/s per watt:

mp​=Prated​2πΔf​

14. Q-V Droop Control

Reactive power-voltage droop is:

V∗=V0​−nq​(Q−Q0​)

For 5% voltage droop at rated reactive power:

ΔV=0.05×Vnom​

In per unit:

Vpu∗​=1.0−nq​(Qpu​−Q0,pu​)

For 5% droop:

nq​=0.05

So at 1 pu reactive power output:

Vpu∗​=0.95

depending on sign convention.

15. Virtual Synchronous Machine / Virtual Inertia

A VSM emulates the swing equation of a synchronous generator:

2Hdtdω​=Pm​−Pe​−D(ω−ω0​)

where:

| Symbol | Meaning |
| --- | --- |
| H | virtual inertia constant, seconds |
| Pm​ | mechanical/input power command |
| Pe​ | measured electrical power |
| D | damping coefficient |
| ω | inverter angular frequency |
| ω0​ | nominal angular frequency |

Discrete implementation:

ω[k]=ω[k−1]+2HΔt​(Pm​−Pe​−D(ω[k−1]−ω0​))

Then:

θ[k]=θ[k−1]+ω[k]Δt

Typical values:

| Parameter | Typical Value |
| --- | --- |
| H | 1–5 s |
| D | 0.5–5 pu |
| Frequency limits | 57–63 Hz |
| RoCoF limit | 0.5–2 Hz/s |

16. Voltage and Frequency Regulation in Island Mode

In island mode:

- The inverter sets the microgrid frequency.

- The inverter sets the voltage magnitude.

- Loads determine actual P and Q.

- Droop or VSM shares load between multiple grid-forming units.

Voltage reference:

vd∗​=V∗ vq∗​=0

Frequency reference:

θ∗=∫ω∗dt

The voltage controller generates current references:

id∗​=Kp,v​(vd∗​−vd​)+Ki,v​∫(vd∗​−vd​)dt iq∗​=Kp,v​(vq∗​−vq​)+Ki,v​∫(vq∗​−vq​)dt

These current references then go to the inner current controller.

17. Virtual Impedance for Fault Current Limiting

Virtual impedance modifies the voltage reference based on inverter current:

vd∗′​=vd∗​−Rv​id​+Xv​iq​ vq∗′​=vq∗​−Rv​iq​−Xv​id​

where:

| Symbol | Meaning |
| --- | --- |
| Rv​ | virtual resistance |
| Xv​ | virtual reactance |
| id​, iq​ | inverter currents |

Virtual impedance helps:

- Limit fault current

- Improve stability

- Improve power sharing

- Dampen oscillations

- Shape inverter output impedance

Fault current limit target:

Ifault,max​=1.1 to 1.5 pu

A practical current limit is:

Imax​=1.2 pu

or for short-duration faults:

Imax​=1.5 pu for 100–200 ms

18. Seamless Transition From Grid-Following to Grid-Forming

The transition is triggered by islanding detection.

Typical islanding detection signals:

- PCC breaker open

- Grid voltage loss

- Rate of change of frequency

- Voltage magnitude below threshold

- Communication command from microgrid controller

Transition logic:

If grid is connected:

operate in grid-following mode

PLL tracks grid angle

P/Q references generate current commands

If islanding detected:

freeze PLL angle

initialize grid-forming angle = PLL angle

initialize grid-forming frequency = PLL frequency

initialize voltage magnitude = measured PCC voltage

ramp from current-source behavior to voltage-source behavior

enable droop / VSM

To avoid transient jumps:

θGFM,0​=θPLL​ ωGFM,0​=ωPLL​ VGFM,0​=∣VPCC​∣

Then slowly ramp voltage reference to nominal:

V∗(t)→1.0 pu

A typical transition time is:

20 ms to 200 ms

Part D — Current Saturation Logic

19. Current Magnitude Limiting

The inverter current command must satisfy:

Icmd​=id∗2​+iq∗2​​

If:

Icmd​>Imax​

then scale or prioritize commands.

20. Active Current Priority

Active current priority means active power delivery is preserved first.

Algorithm:

- Limit id∗​ first to Imax​.

- Use remaining current capacity for iq∗​.

idlim​=sat(id∗​,−Imax​,Imax​) iq,max​=Imax2​−idlim2​​ iqlim​=sat(iq∗​,−iq,max​,iq,max​)

Purpose:

- Maintains real power output.

- Useful for energy export or grid-following P priority.

- May reduce voltage support during faults.

21. Reactive Current Priority

Reactive current priority means voltage support is preserved first.

Algorithm:

- Limit iq∗​ first.

- Use remaining current capacity for id∗​.

iqlim​=sat(iq∗​,−Imax​,Imax​) id,max​=Imax2​−iqlim2​​ idlim​=sat(id∗​,−id,max​,id,max​)

Purpose:

- Supports grid voltage during faults.

- Common in grid-code fault ride-through behavior.

- Active power may be reduced.

22. Fault Current Limiting

During faults:

If voltage dip is detected:

enable fault mode

reduce active current if reactive priority is enabled

inject reactive current according to voltage deviation

limit total positive + negative sequence current

A typical voltage support law is:

iq∗​=KFRT​(1−Vpu​)

where:

KFRT​=2 to 4 pu current / pu voltage

Then apply:

∣I∣≤1.1 to 1.5 pu

23. Negative Sequence Injection During Faults

For unbalanced faults:

Ineg∗​=Kneg​Vneg​

Apply a current split:

Itotal2​=Ipos2​+Ineg2​

Limit condition:

Ipos2​+Ineg2​≤Imax2​

If the sum exceeds the limit, reduce currents according to priority.

Part E — MV Transformer Model

24. Transformer Specification

Model the integrated MV transformer:

| Parameter | Typical Value |
| --- | --- |
| Rating | 3000 kVA |
| LV voltage | 690 V |
| MV voltage | 13.2 kV |
| Frequency | 60 Hz |
| Impedance | 6–8% |
| X/R ratio | 8–15 |
| Connection | Dyn1, Dyn11, or Yg-Δ depending on project |
| Core saturation | Enabled for energization studies |

A common utility interconnection configuration is:

LV: Delta or grounded wye

MV: Grounded wye

One practical choice:

690 V side: Delta

13.2 kV side: Grounded Wye

This helps block zero-sequence current from propagating through the inverter side.

25. Transformer Impedance Calculation

Given:

Zpu​=0.06 to 0.08

Assume:

Zpu​=0.07

X/R ratio:

RX​=10

Then:

Zpu​=Rpu2​+Xpu2​​

and:

Xpu​=10Rpu​

So:

Zpu​=Rpu​1+102​ Rpu​=101​Zpu​​ Rpu​=10.050.07​=0.00697 Xpu​=0.0697

Transformer leakage inductance:

L=ω0​Xpu​Zbase​​

where:

Zbase​=Sbase​VLL2​​

On the 13.2 kV, 3 MVA base:

Zbase,MV​=3×106132002​ Zbase,MV​=58.08Ω

Therefore:

R=0.00697×58.08=0.405Ω X=0.0697×58.08=4.05Ω L=2π604.05​ L=10.74 mH

26. Transformer Inrush and Saturation

For energization studies, include:

- Nonlinear magnetizing branch

- Residual flux

- Core saturation knee point

- Closing angle sensitivity

- Remanence initialization

Typical saturation data:

| Flux pu | Magnetizing current pu |
| --- | --- |
| 0.90 | 0.005 |
| 1.00 | 0.010 |
| 1.10 | 0.020 |
| 1.20 | 0.050 |
| 1.30 | 0.150 |
| 1.40 | 0.500 |
| 1.50 | 1.500 |

In PSCAD:

- Use a three-phase transformer component with saturation enabled.

- Enter magnetizing curve.

- Set residual flux if studying worst-case energization.

- Use controlled breaker closing angles.

Worst-case inrush occurs when:

- Closing occurs near voltage zero crossing.

- Residual flux is aligned with prospective flux.

- Transformer is lightly loaded.

Unit Controller Code

The following is controller-style pseudocode suitable for implementation inside a PSCAD User Defined Component, Fortran block, or C-script style control block.

It is not tied to one exact PSCAD component syntax, but the structure maps directly to PSCAD control blocks.

27. Unit Controller Purpose

The unit controller manages the local inverter. It handles:

- Measurement filtering

- PLL operation

- P/Q calculation

- Grid-following current reference generation

- Grid-forming voltage and frequency generation

- Mode selection

- Fault current limiting

- Current saturation

- PWM voltage command generation

28. Unit Controller Inputs and Outputs

Inputs

| Signal | Description |
| --- | --- |
| Va, Vb, Vc | PCC phase voltages |
| Ia, Ib, Ic | inverter output currents |
| P_set | active power setpoint |
| Q_set | reactive power setpoint |
| PF_set | power factor setpoint |
| V_set | voltage setpoint |
| F_set | frequency setpoint |
| grid_connected | breaker/grid status |
| islanding_detected | islanding flag |
| mode_cmd | GFL or GFM command |
| priority_mode | active or reactive current priority |
| fault_flag | voltage dip or fault flag |

Outputs

| Signal | Description |
| --- | --- |
| Vd_cmd, Vq_cmd | dq voltage command |
| Va_cmd, Vb_cmd, Vc_cmd | abc voltage command |
| Id_ref, Iq_ref | current references |
| theta | controller electrical angle |
| freq | inverter frequency |
| mode_status | active operating mode |

29. Unit Controller Pseudocode

/* ============================================================

PCS3440 Unit Controller Pseudocode

Suitable for PSCAD User Component Implementation

============================================================ */

/* ---------- Constants ---------- */

const double PI = 3.141592653589793;

const double F_NOM = 60.0;

const double W_NOM = 2.0 * PI * F_NOM;

const double S_BASE = 3.44e6;

const double VLL_BASE_LV = 690.0;

const double I_BASE_LV = S_BASE / (sqrt(3.0) * VLL_BASE_LV);

const double I_MAX_NORMAL = 1.10;   /* pu */

const double I_MAX_FAULT  = 1.50;   /* pu */

const double V_FAULT_ENTER = 0.90;  /* pu */

const double V_FAULT_EXIT  = 0.95;  /* pu */

/* ---------- Tunable Parameters ---------- */

double pll_bw_hz = 20.0;

double pll_zeta = 0.707;

double current_bw_hz = 300.0;

double L_filter_pu = 0.10;

double R_filter_pu = 0.005;

double P_ramp_rate_MW_per_s = 1.0;

double droop_P_percent = 5.0;

double droop_Q_percent = 5.0;

double H_virtual = 2.0;

double D_virtual = 1.0;

double R_virtual = 0.02;

double X_virtual = 0.08;

double K_frt = 2.0;

double K_neg = 1.0;

/* ---------- States ---------- */

double theta_pll = 0.0;

double omega_pll = W_NOM;

double pll_integrator = 0.0;

double id_integrator = 0.0;

double iq_integrator = 0.0;

double vd_integrator = 0.0;

double vq_integrator = 0.0;

double theta_gfm = 0.0;

double omega_gfm = W_NOM;

double P_cmd_ramped = 0.0;

double Q_cmd_ramped = 0.0;

int mode_actual = 0;

/* 0 = Grid-Following, 1 = Grid-Forming */

int fault_active = 0;

/* ============================================================

Utility Functions

============================================================ */

double saturate(double x, double xmin, double xmax)

{

if (x > xmax) return xmax;

if (x < xmin) return xmin;

return x;

}

double ramp_limit(double target, double previous, double rate_per_sec, double dt)

{

double delta_max = rate_per_sec * dt;

double delta = target - previous;

delta = saturate(delta, -delta_max, delta_max);

return previous + delta;

}

void abc_to_dq(

double a, double b, double c,

double theta,

double *d, double *q)

{

double cos_t = cos(theta);

double sin_t = sin(theta);

double cos_t_120 = cos(theta - 2.0 * PI / 3.0);

double sin_t_120 = sin(theta - 2.0 * PI / 3.0);

double cos_t_240 = cos(theta + 2.0 * PI / 3.0);

double sin_t_240 = sin(theta + 2.0 * PI / 3.0);

*d = (2.0 / 3.0) * (a * cos_t + b * cos_t_120 + c * cos_t_240);

*q = -(2.0 / 3.0) * (a * sin_t + b * sin_t_120 + c * sin_t_240);

}

void dq_to_abc(

double d, double q,

double theta,

double *a, double *b, double *c)

{

*a = d * cos(theta) - q * sin(theta);

*b = d * cos(theta - 2.0 * PI / 3.0) - q * sin(theta - 2.0 * PI / 3.0);

*c = d * cos(theta + 2.0 * PI / 3.0) - q * sin(theta + 2.0 * PI / 3.0);

}

void priority_current_limiter(

double id_ref,

double iq_ref,

double imax,

int priority_mode,

double *id_lim,

double *iq_lim)

{

double id_max;

double iq_max;

if (priority_mode == 0)

{

/* Active current priority */

*id_lim = saturate(id_ref, -imax, imax);

iq_max = sqrt(fmax(imax * imax - (*id_lim) * (*id_lim), 0.0));

*iq_lim = saturate(iq_ref, -iq_max, iq_max);

}

else

{

/* Reactive current priority */

*iq_lim = saturate(iq_ref, -imax, imax);

id_max = sqrt(fmax(imax * imax - (*iq_lim) * (*iq_lim), 0.0));

*id_lim = saturate(id_ref, -id_max, id_max);

}

}

30. Main Unit Controller Execution Loop

This loop is executed every PSCAD control time step.

void unit_controller_step(

double Va_pu,

double Vb_pu,

double Vc_pu,

double Ia_pu,

double Ib_pu,

double Ic_pu,

double P_set_pu,

double Q_set_pu,

double PF_set,

double V_set_pu,

double F_set_hz,

int pf_mode_enable,

int grid_connected,

int islanding_detected,

int mode_cmd,

int priority_mode,

double dt,

double *Va_cmd_pu,

double *Vb_cmd_pu,

double *Vc_cmd_pu,

double *Id_ref_out,

double *Iq_ref_out,

double *freq_out,

int *mode_status)

{

double vd_pll, vq_pll;

double id_meas, iq_meas;

double P_meas, Q_meas;

double Vmag_pu;

double pll_bw_rad;

double Kp_pll, Ki_pll;

double current_bw_rad;

double Kp_i, Ki_i;

double id_ref, iq_ref;

double id_lim, iq_lim;

double vd_cmd, vq_cmd;

double vd_ref_gfm, vq_ref_gfm;

double Imax;

/* ========================================================

1. PLL dq Transformation

======================================================== */

abc_to_dq(Va_pu, Vb_pu, Vc_pu, theta_pll, &vd_pll, &vq_pll);

abc_to_dq(Ia_pu, Ib_pu, Ic_pu, theta_pll, &id_meas, &iq_meas);

Vmag_pu = sqrt(vd_pll * vd_pll + vq_pll * vq_pll);

/* ========================================================

2. Fault Detection

======================================================== */

if (Vmag_pu < V_FAULT_ENTER)

{

fault_active = 1;

}

else if (Vmag_pu > V_FAULT_EXIT)

{

fault_active = 0;

}

if (fault_active)

{

Imax = I_MAX_FAULT;

}

else

{

Imax = I_MAX_NORMAL;

}

/* ========================================================

3. SRF PLL

Purpose:

Synchronizes inverter to grid angle in grid-following mode.

======================================================== */

pll_bw_rad = 2.0 * PI * pll_bw_hz;

Kp_pll = 2.0 * pll_zeta * pll_bw_rad;

Ki_pll = pll_bw_rad * pll_bw_rad;

if (grid_connected && mode_actual == 0)

{

pll_integrator += Ki_pll * vq_pll * dt;

omega_pll = W_NOM + Kp_pll * vq_pll + pll_integrator;

omega_pll = saturate(

omega_pll,

2.0 * PI * 55.0,

2.0 * PI * 65.0

);

theta_pll += omega_pll * dt;

if (theta_pll > 2.0 * PI)

theta_pll -= 2.0 * PI;

if (theta_pll < 0.0)

theta_pll += 2.0 * PI;

}

/* ========================================================

4. Power Calculation

Purpose:

Calculates instantaneous active and reactive power.

======================================================== */

P_meas = 1.5 * (vd_pll * id_meas + vq_pll * iq_meas);

Q_meas = 1.5 * (vq_pll * id_meas - vd_pll * iq_meas);

/* ========================================================

5. Mode Selection and Transition

Purpose:

Switch between GFL and GFM without phase jump.

======================================================== */

if (islanding_detected || !grid_connected || mode_cmd == 1)

{

if (mode_actual == 0)

{

theta_gfm = theta_pll;

omega_gfm = omega_pll;

}

mode_actual = 1;

}

else

{

mode_actual = 0;

}

/* ========================================================

6. Active Power Ramp Limiter

Purpose:

Prevents sudden power command changes.

======================================================== */

P_cmd_ramped = ramp_limit(

P_set_pu,

P_cmd_ramped,

P_ramp_rate_MW_per_s / 3.44,

dt

);

Q_cmd_ramped = Q_set_pu;

/* ========================================================

7. Grid-Following Mode

======================================================== */

if (mode_actual == 0)

{

double vd_safe;

vd_safe = fmax(fabs(vd_pll), 0.2);

id_ref = (2.0 / 3.0) * P_cmd_ramped / vd_safe;

if (pf_mode_enable)

{

double angle_pf;

double Q_from_pf;

PF_set = saturate(PF_set, 0.1, 1.0);

angle_pf = acos(PF_set);

Q_from_pf = P_cmd_ramped * tan(angle_pf);

iq_ref = -(2.0 / 3.0) * Q_from_pf / vd_safe;

}

else

{

iq_ref = -(2.0 / 3.0) * Q_cmd_ramped / vd_safe;

}

/* Fault ride-through reactive current injection */

if (fault_active)

{

double iq_frt;

iq_frt = K_frt * (1.0 - Vmag_pu);

/*

Reactive priority is normally preferred during voltage dips.

Sign must be verified according to PSCAD Q convention.

*/

iq_ref = iq_ref + iq_frt;

}

priority_current_limiter(

id_ref,

iq_ref,

Imax,

priority_mode,

&id_lim,

&iq_lim

);

current_bw_rad = 2.0 * PI * current_bw_hz;

Kp_i = L_filter_pu * current_bw_rad;

Ki_i = R_filter_pu * current_bw_rad;

id_integrator += Ki_i * (id_lim - id_meas) * dt;

iq_integrator += Ki_i * (iq_lim - iq_meas) * dt;

id_integrator = saturate(id_integrator, -2.0, 2.0);

iq_integrator = saturate(iq_integrator, -2.0, 2.0);

vd_cmd =

vd_pll

+ Kp_i * (id_lim - id_meas)

+ id_integrator

- W_NOM * L_filter_pu * iq_meas;

vq_cmd =

vq_pll

+ Kp_i * (iq_lim - iq_meas)

+ iq_integrator

+ W_NOM * L_filter_pu * id_meas;

dq_to_abc(

vd_cmd,

vq_cmd,

theta_pll,

Va_cmd_pu,

Vb_cmd_pu,

Vc_cmd_pu

);

*freq_out = omega_pll / (2.0 * PI);

}

/* ========================================================

8. Grid-Forming Mode

======================================================== */

else

{

double mf;

double nq;

double P_error;

double accel;

double V_droop;

/*

P-f droop:

5% droop means 3 Hz change at 1 pu P.

*/

mf = (droop_P_percent / 100.0) * F_NOM;

/*

Q-V droop:

5% voltage change at 1 pu Q.

*/

nq = droop_Q_percent / 100.0;

/*

VSM swing equation:

2H*dω/dt = Pset - Pmeas - D*(ω - ω0)

*/

P_error = P_cmd_ramped - P_meas;

accel =

(P_error - D_virtual * ((omega_gfm - W_NOM) / W_NOM))

/ (2.0 * H_virtual);

omega_gfm += accel * W_NOM * dt;

/*

Optional droop contribution.

This can be blended with VSM or used alone.

*/

omega_gfm =

W_NOM

- 2.0 * PI * mf * (P_meas - P_cmd_ramped)

+ (omega_gfm - W_NOM);

omega_gfm = saturate(

omega_gfm,

2.0 * PI * 57.0,

2.0 * PI * 63.0

);

theta_gfm += omega_gfm * dt;

if (theta_gfm > 2.0 * PI)

theta_gfm -= 2.0 * PI;

if (theta_gfm < 0.0)

theta_gfm += 2.0 * PI;

/*

Q-V droop.

*/

V_droop = V_set_pu - nq * (Q_meas - Q_cmd_ramped);

V_droop = saturate(V_droop, 0.90, 1.10);

vd_ref_gfm = V_droop;

vq_ref_gfm = 0.0;

/*

Virtual impedance:

v* = v_ref - Z_virtual * i

*/

vd_cmd =

vd_ref_gfm

- R_virtual * id_meas

+ X_virtual * iq_meas;

vq_cmd =

vq_ref_gfm

- R_virtual * iq_meas

- X_virtual * id_meas;

/*

During fault, increase virtual impedance to limit current.

*/

if (fault_active)

{

double scale;

scale = sqrt(id_meas * id_meas + iq_meas * iq_meas) / Imax;

if (scale > 1.0)

{

vd_cmd = vd_cmd / scale;

vq_cmd = vq_cmd / scale;

}

}

dq_to_abc(

vd_cmd,

vq_cmd,

theta_gfm,

Va_cmd_pu,

Vb_cmd_pu,

Vc_cmd_pu

);

id_lim = id_meas;

iq_lim = iq_meas;

*freq_out = omega_gfm / (2.0 * PI);

}

/* ========================================================

9. Output Assignments

======================================================== */

*Id_ref_out = id_lim;

*Iq_ref_out = iq_lim;

*mode_status = mode_actual;

}

Microgrid Controller Code

31. Microgrid Controller Purpose

The microgrid controller is a higher-level controller. It does not directly generate PWM commands. Instead, it sends commands to each inverter unit.

Its purposes are:

- Detect grid-connected or islanded operation.

- Dispatch active power setpoints.

- Dispatch reactive power or voltage setpoints.

- Coordinate grid-following and grid-forming modes.

- Manage black start or resynchronization.

- Share load among multiple inverters.

- Enforce ramp-rate limits.

- Send fault ride-through priority commands.

- Coordinate reconnection to the grid.

32. Microgrid Controller Inputs and Outputs

Inputs

| Signal | Description |
| --- | --- |
| P_load | total microgrid load |
| Q_load | total reactive load |
| P_grid | power imported/exported at PCC |
| Q_grid | reactive exchange at PCC |
| V_pcc | PCC voltage |
| F_pcc | PCC frequency |
| grid_breaker_status | grid breaker state |
| islanding_relay | islanding detection signal |
| fault_status | system fault flag |
| unit_available[i] | inverter unit availability |
| SOC[i] | energy storage SOC if applicable |

Outputs

| Signal | Description |
| --- | --- |
| P_set[i] | active power command per inverter |
| Q_set[i] | reactive power command per inverter |
| V_set[i] | voltage command per inverter |
| F_set[i] | frequency command per inverter |
| mode_cmd[i] | GFL or GFM command |
| priority_mode[i] | active or reactive current priority |

33. Microgrid Controller Pseudocode

/* ============================================================

PCS3440 Microgrid Controller Pseudocode

============================================================ */

const int N_UNITS = 4;

const double P_UNIT_MAX = 3.44;  /* MW */

const double Q_UNIT_MAX = 3.44;  /* MVAr approximately */

const double F_NOM_MG = 60.0;

const double V_NOM_MG = 1.0;

const double V_SYNC_MAX_ERROR = 0.03;  /* pu */

const double F_SYNC_MAX_ERROR = 0.10;  /* Hz */

const double ANGLE_SYNC_MAX_ERROR = 10.0; /* degrees */

const double P_RAMP_MW_PER_S = 1.0;

const double Q_RAMP_MVAR_PER_S = 1.0;

double P_set_prev[N_UNITS];

double Q_set_prev[N_UNITS];

int microgrid_state = 0;

/*

0 = Grid-connected

1 = Islanded

2 = Resynchronizing

3 = Black-start

*/

double mg_ramp_limit(double target, double previous, double rate, double dt)

{

double delta;

double delta_max;

delta_max = rate * dt;

delta = target - previous;

if (delta > delta_max)

delta = delta_max;

if (delta < -delta_max)

delta = -delta_max;

return previous + delta;

}

void microgrid_controller_step(

double P_load_MW,

double Q_load_MVAR,

double P_grid_MW,

double Q_grid_MVAR,

double V_pcc_pu,

double F_pcc_Hz,

double angle_error_deg,

int grid_breaker_closed,

int islanding_relay,

int fault_status,

int unit_available[N_UNITS],

double SOC[N_UNITS],

double dt,

double P_set[N_UNITS],

double Q_set[N_UNITS],

double V_set[N_UNITS],

double F_set[N_UNITS],

int mode_cmd[N_UNITS],

int priority_mode[N_UNITS],

int *close_grid_breaker_cmd)

{

int i;

int available_count;

double total_weight;

double weight[N_UNITS];

available_count = 0;

total_weight = 0.0;

*close_grid_breaker_cmd = 0;

/* ========================================================

1. Determine Available Units

Purpose:

Only dispatch units that are healthy and available.

======================================================== */

for (i = 0; i < N_UNITS; i++)

{

if (unit_available[i])

{

available_count++;

/*

If energy storage is present, SOC can influence dispatch.

Higher SOC receives higher active power responsibility.

*/

weight[i] = fmax(SOC[i], 0.10);

total_weight += weight[i];

}

else

{

weight[i] = 0.0;

}

}

if (available_count == 0)

{

for (i = 0; i < N_UNITS; i++)

{

P_set[i] = 0.0;

Q_set[i] = 0.0;

mode_cmd[i] = 0;

}

return;

}

/* ========================================================

2. Microgrid State Machine

Purpose:

Select grid-connected, islanded, or resynchronizing mode.

======================================================== */

if (!grid_breaker_closed || islanding_relay)

{

microgrid_state = 1;

}

else

{

if (microgrid_state != 2)

{

microgrid_state = 0;

}

}

/* ========================================================

3. Grid-Connected Dispatch

Purpose:

Units operate in grid-following mode and track P/Q commands.

======================================================== */

if (microgrid_state == 0)

{

double P_export_target;

double Q_exchange_target;

P_export_target = P_load_MW - P_grid_MW;

Q_exchange_target = Q_load_MVAR - Q_grid_MVAR;

for (i = 0; i < N_UNITS; i++)

{

if (unit_available[i])

{

double P_share;

double Q_share;

P_share = P_export_target * weight[i] / total_weight;

Q_share = Q_exchange_target / available_count;

P_share = fmin(fmax(P_share, -P_UNIT_MAX), P_UNIT_MAX);

Q_share = fmin(fmax(Q_share, -Q_UNIT_MAX), Q_UNIT_MAX);

P_set[i] = mg_ramp_limit(

P_share,

P_set_prev[i],

P_RAMP_MW_PER_S,

dt

);

Q_set[i] = mg_ramp_limit(

Q_share,

Q_set_prev[i],

Q_RAMP_MVAR_PER_S,

dt

);

V_set[i] = V_NOM_MG;

F_set[i] = F_NOM_MG;

mode_cmd[i] = 0;       /* Grid-following */

priority_mode[i] = 0;  /* Active priority */

}

else

{

P_set[i] = 0.0;

Q_set[i] = 0.0;

V_set[i] = V_NOM_MG;

F_set[i] = F_NOM_MG;

mode_cmd[i] = 0;

priority_mode[i] = 0;

}

}

}

/* ========================================================

4. Islanded Dispatch

Purpose:

At least one unit must form voltage and frequency.

======================================================== */

else if (microgrid_state == 1)

{

double P_required;

double Q_required;

P_required = P_load_MW;

Q_required = Q_load_MVAR;

for (i = 0; i < N_UNITS; i++)

{

if (unit_available[i])

{

double P_share;

double Q_share;

P_share = P_required * weight[i] / total_weight;

Q_share = Q_required / available_count;

P_share = fmin(fmax(P_share, -P_UNIT_MAX), P_UNIT_MAX);

Q_share = fmin(fmax(Q_share, -Q_UNIT_MAX), Q_UNIT_MAX);

P_set[i] = mg_ramp_limit(

P_share,

P_set_prev[i],

P_RAMP_MW_PER_S,

dt

);

Q_set[i] = mg_ramp_limit(

Q_share,

Q_set_prev[i],

Q_RAMP_MVAR_PER_S,

dt

);

V_set[i] = V_NOM_MG;

F_set[i] = F_NOM_MG;

mode_cmd[i] = 1;       /* Grid-forming */

priority_mode[i] = 1;  /* Reactive priority */

}

else

{

P_set[i] = 0.0;

Q_set[i] = 0.0;

V_set[i] = V_NOM_MG;

F_set[i] = F_NOM_MG;

mode_cmd[i] = 0;

priority_mode[i] = 0;

}

}

}

/* ========================================================

5. Fault Behavior

Purpose:

During faults, prioritize reactive current support.

======================================================== */

if (fault_status)

{

for (i = 0; i < N_UNITS; i++)

{

if (unit_available[i])

{

priority_mode[i] = 1;  /* Reactive priority */

}

}

}

/* ========================================================

6. Resynchronization Logic

Purpose:

Reconnect islanded microgrid to utility grid safely.

======================================================== */

if (microgrid_state == 1 && grid_breaker_closed == 0)

{

if (

fabs(V_pcc_pu - V_NOM_MG) < V_SYNC_MAX_ERROR &&

fabs(F_pcc_Hz - F_NOM_MG) < F_SYNC_MAX_ERROR &&

fabs(angle_error_deg) < ANGLE_SYNC_MAX_ERROR

)

{

microgrid_state = 2;

}

}

if (microgrid_state == 2)

{

*close_grid_breaker_cmd = 1;

for (i = 0; i < N_UNITS; i++)

{

if (unit_available[i])

{

/*

After reconnection, transition units back to grid-following.

*/

mode_cmd[i] = 0;

}

}

microgrid_state = 0;

}

/* ========================================================

7. Store Previous Commands

======================================================== */

for (i = 0; i < N_UNITS; i++)

{

P_set_prev[i] = P_set[i];

Q_set_prev[i] = Q_set[i];

}

}

Step-by-Step PSCAD Implementation Procedure

34. Step 1 — Create the PSCAD Project

In PSCAD v5.0.2:

- Open PSCAD.

- Create a new project.

- Set system frequency to 60 Hz.

- Set EMTDC time step.

Recommended starting values:

| Simulation Type | Time Step |
| --- | --- |
| Average inverter model | 25–50 µs |
| Detailed switching model | 1–5 µs |
| Transformer energization | 1–10 µs |
| Control-only validation | 25–100 µs |

35. Step 2 — Build the AC Network

Create:

- 13.2 kV grid source.

- Grid equivalent impedance.

- PCC bus.

- 690 V / 13.2 kV transformer.

- 690 V inverter bus.

- Filter.

- Inverter equivalent.

Grid impedance for SCR studies:

SCR=Sinv​Ssc​​

Therefore:

Ssc​=SCR×Sinv​

Grid equivalent impedance:

Zgrid,pu​=SCR1​

For weak grid SCR = 2:

Zgrid,pu​=0.5

For SCR = 3:

Zgrid,pu​=0.333

For SCR = 5:

Zgrid,pu​=0.2

Use these cases to test PLL stability.

36. Step 3 — Add Measurements

Measure:

- Three-phase PCC voltage

- Three-phase inverter current

- Active power

- Reactive power

- RMS voltage

- Frequency

- Positive sequence voltage

- Negative sequence voltage

- Breaker status

Use low-pass filters on measured power:

GLPF​(s)=s+ωc​ωc​​

Typical cutoff:

fc​=20 to 50 Hz

37. Step 4 — Implement SRF-PLL

PSCAD blocks required:

- abc-to-dq transform

- PI controller

- integrator for angle

- angle wrap block

- sine/cosine generation

Use:

Kp,PLL​=2ζωBW​ Ki,PLL​=ωBW2​

Test PLL bandwidths:

| Case | Bandwidth |
| --- | --- |
| Weak grid | 10 Hz |
| Moderate grid | 20 Hz |
| Strong grid | 30–50 Hz |

38. Step 5 — Implement Grid-Following Current Control

Build:

- P-to-id​ reference block

- Q-to-iq​ reference block

- Current PI controllers

- dq decoupling terms

- Voltage feedforward

- Current limiter

- dq-to-abc transform

Use:

id∗​=3vd​2P∗​ iq∗​=−3vd​2Q∗​

Then:

vd∗​=vd​+PI(id∗​−id​)−ωLiq​ vq∗​=vq​+PI(iq∗​−iq​)+ωLid​

39. Step 6 — Implement Active Power Ramp Limiter

Use a PSCAD limiter and memory block.

At each control step:

Pcmd​[k]=Pcmd​[k−1]+ΔP

where:

ΔP=sat(Pset​−Pcmd​[k−1],−RP​Δt,RP​Δt)

Make R_P user configurable in MW/s.

40. Step 7 — Implement Reactive Power or PF Mode

Add a selector:

If Q mode:

Q_ref = Q_set

If PF mode:

Q_ref = P_ref * tan(acos(PF_set))

Then calculate:

iq∗​=−2Q∗/3vd​​

41. Step 8 — Implement Negative Sequence Control

In PSCAD:

- Use positive/negative sequence extraction.

- Transform positive sequence using +θ.

- Transform negative sequence using −θ.

- Control positive and negative sequence current separately.

- Reconstruct abc current or voltage command.

Use:

ineg∗​=Kneg​vneg​

Then limit:

Ipos2​+Ineg2​≤Imax2​

42. Step 9 — Implement Grid-Forming Droop Control

In PSCAD, create a GFM subsystem.

Inputs:

- Measured P

- Measured Q

- P setpoint

- Q setpoint

- V setpoint

- Frequency setpoint

Equations:

f∗=f0​−mf​(P−P0​)

V∗=V0​−nq​(Q−Q0​)

Integrate frequency:

θ=∫2πf∗dt

Generate voltage reference:

vd∗​=V∗ vq∗​=0

43. Step 10 — Implement VSM

Use swing equation:

2Hdtdω​=P∗−P−D(ω−ω0​)

In PSCAD:

- Subtract measured P from P command.

- Add damping term.

- Divide by $2H$.

- Integrate to get ω.

- Integrate ω to get θ.

44. Step 11 — Implement Virtual Impedance

Use:

vd∗′​=vd∗​−Rv​id​+Xv​iq​

vq∗′​=vq∗​−Rv​iq​−Xv​id​

Increase Rv​ or Xv​ during faults to limit current.

45. Step 12 — Implement Seamless Transfer

Add transition logic:

If islanding event occurs:

theta_gfm = theta_pll

omega_gfm = omega_pll

V_gfm = measured PCC voltage

switch control mode from GFL to GFM

ramp voltage to nominal

Avoid:

- Phase discontinuity

- Voltage magnitude jump

- Frequency jump

- PI integrator windup

Freeze or reset integrators during mode transfer.

46. Step 13 — Implement Transformer

In PSCAD:

- Add three-phase transformer.

- Set rating to 3000 kVA.

- Set voltage ratio to 0.69 / 13.2 kV.

- Set leakage impedance to 6–8%.

- Use X/R ratio around 10.

- Select winding connection.

- Enable saturation for inrush studies.

- Add breaker for energization.

Recommended starting values:

| Parameter | Value |
| --- | --- |
| Rating | 3 MVA |
| LV | 690 V |
| MV | 13.2 kV |
| Z | 7% |
| X/R | 10 |
| R pu | 0.00697 |
| X pu | 0.0697 |

47. Step 14 — Simulation Test Cases

Run the following validation cases.

Case 1 — PLL stability

| Test | Condition |
| --- | --- |
| Strong grid | SCR = 10 |
| Moderate grid | SCR = 5 |
| Weak grid | SCR = 2–3 |
| PLL bandwidth | 10, 20, 50 Hz |

Check:

- PLL angle

- PLL frequency

- dq voltage

- Power oscillations

- Current oscillations

Expected:

- 10–20 Hz should be more stable in weak grids.

- 50 Hz may oscillate under weak-grid conditions.

Case 2 — Current loop response

Apply step in id∗​ or iq∗​.

Target:

ts​<5 ms

Check:

- Rise time

- Overshoot

- Settling time

- dq decoupling effectiveness

Case 3 — P tracking

Apply active power step:

P_set: 0.5 pu → 1.0 pu

Ramp rate: 1 MW/s

Verify:

- Ramp rate is respected.

- No current saturation in normal operation.

- No DC-link or voltage instability.

Case 4 — Q or PF mode

Test:

Q_set: 0 pu → 0.5 pu

PF_set: 1.0 → 0.95 lagging

Verify:

- Reactive power sign convention.

- Current limit behavior.

- Voltage response.

Case 5 — Unbalanced grid

Apply:

- Single-line-to-ground fault

- Line-line fault

- Voltage unbalance

Verify:

- Negative sequence voltage detection

- Negative sequence current injection

- Current limit enforcement

Case 6 — Islanding transition

Start grid-connected in GFL mode.

Then open PCC breaker.

Verify:

- GFL to GFM transition

- No phase jump

- Voltage maintained

- Frequency maintained

- Load supplied

Case 7 — Fault current limiting

Apply three-phase and single-phase faults.

Verify:

Ifault​≤1.1 to 1.5 pu

Check:

- Active/reactive priority behavior

- Virtual impedance response

- Negative-sequence injection

Case 8 — Transformer energization

Test transformer energization with:

- No residual flux

- Positive residual flux

- Negative residual flux

- Different breaker closing angles

Check:

- Inrush current magnitude

- Harmonics

- DC offset

- Saturation behavior

Recommended Parameter Summary

48. Initial Controller Parameters

| Parameter | Recommended Starting Value |
| --- | --- |
| PLL bandwidth | 10–20 Hz weak grid, 30–50 Hz strong grid |
| PLL damping | 0.707 |
| Current loop bandwidth | 300 Hz |
| Current response target | <5 ms |
| P ramp rate | 0.5–5 MW/s |
| Normal current limit | 1.1 pu |
| Fault current limit | 1.2–1.5 pu |
| P-f droop | 4–5% |
| Q-V droop | 5% |
| Virtual inertia H | 1–5 s |
| Damping D | 0.5–5 pu |
| Virtual R | 0.01–0.05 pu |
| Virtual X | 0.05–0.15 pu |
| Transformer impedance | 6–8% |
| Transformer X/R | 8–15 |

Purpose of Each Major Block

49. Controller Block Purpose Summary

| Block | Purpose |
| --- | --- |
| SRF-PLL | Synchronizes inverter with grid voltage angle |
| abc/dq transform | Converts sinusoidal signals to DC quantities for control |
| P/Q calculator | Computes real and reactive power |
| P ramp limiter | Prevents sudden real power changes |
| Q/PF controller | Generates reactive current command |
| Current PI controller | Tracks dq current references |
| Decoupling terms | Reduce cross-coupling between d and q axes |
| Current limiter | Keeps inverter within semiconductor limits |
| Negative sequence controller | Handles unbalanced grid voltage/faults |
| Droop controller | Allows grid-forming power sharing |
| VSM controller | Emulates inertia and damping |
| Virtual impedance | Limits current and improves stability |
| Mode transition logic | Switches safely between GFL and GFM |
| Transformer model | Represents voltage step-up and magnetic behavior |
| Microgrid controller | Supervisory dispatch and mode coordination |

Practical PSCAD Notes

50. Implementation Tips

- Start with per-unit signals.
This makes tuning easier and avoids scaling mistakes.

- Validate each block separately.
Do not build the full model at once.

- Begin with average inverter model.
Add switching only after the controls are stable.

- Check sign conventions carefully.
Especially for:

  - Reactive power

  - dq transformation

  - PLL q-axis error

  - Transformer winding phase shift

- Use anti-windup in every PI controller.

- Limit PLL frequency.

- Freeze or reset integrators during mode changes.

- Use slower PLL for weak grids.

- Use reactive current priority during voltage faults.

- Test unbalanced faults separately from balanced faults.

Final Recommended Build Order

51. Suggested PSCAD Development Sequence

Build the model in this order:

- Create base network and transformer.

- Add average-value inverter.

- Add abc/dq and dq/abc transformations.

- Add PLL.

- Add current controller.

- Add P/Q measurement.

- Add P and Q reference generation.

- Add ramp limiter.

- Add current saturation.

- Test grid-following mode.

- Add fault detection.

- Add negative sequence extraction.

- Add negative sequence current control.

- Add droop controller.

- Add VSM controller.

- Add virtual impedance.

- Test grid-forming island mode.

- Add transition logic.

- Add transformer saturation.

- Run validation cases.

This sequence avoids debugging all subsystems at once and helps isolate numerical, scaling, and sign-convention errors.