DELTA ENGINEERING

S-UI-03: Utility Metering & CT/PT Specification Package

Revenue-Grade Metering | Instrument Transformer Selection | Communication & SCADA Integration

| Document Number: | S-UI-03 |
| --- | --- |
| Revision: | Rev 1.0 |
| Date: | June 25, 2026 |
| Prepared For: | Delta Engineering – East Coast Microgrid Program |
| Classification: | Internal Technical Specification |
| Status: | ISSUED FOR USE |

# Table of Contents

Table of Contents	2

Executive Summary	5

Section 1: Standards Review	6

1.1 ANSI C12.1 – Code for Electricity Metering	6

1.2 ANSI C12.20 – Accuracy Classes 0.2 and 0.5	6

1.3 IEEE C57.13 – Instrument Transformers	7

1.3.1 Accuracy Classes Under IEEE C57.13	7

1.3.2 Burden Ratings	7

1.4 IEC 61869 – Instrument Transformers (International)	8

1.5 IEC 62056 – DLMS/COSEM Data Exchange	8

Section 2: Regional Metering Rules	10

2.1 NYISO Territory	10

2.2 ISO-NE Territory (CT, MA, ME, NH, RI, VT)	10

2.3 PJM Territory (DE, MD, NJ, PA, VA, NC, WV, IL, IN, OH, MI)	11

2.4 MISO-East Territory (MI, IN, MN, IA)	11

2.5 Regional Metering Summary Matrix	11

Section 3: Utility Revenue Meter Specifications	13

3.1 Con Edison (ConEd) – New York City and Westchester	13

3.2 National Grid – New York, Massachusetts, Rhode Island	13

3.3 Eversource – Connecticut, Massachusetts, New Hampshire	14

3.4 Duke Energy – North Carolina, South Carolina, Florida	14

3.5 Dominion Energy – Virginia, North Carolina	15

3.6 DTE Energy – Michigan	15

3.7 ComEd – Illinois	16

3.8 PSE&G – New Jersey	16

3.9 BGE – Maryland	16

3.10 PPL – Pennsylvania	17

3.11 Utility Revenue Meter Requirements Summary Matrix	17

Section 4: CT/PT Selection Matrix	18

4.1 MV Applications – 15 kV Class	18

4.2 MV Applications – 35 kV Class	18

4.3 Burden Calculations	19

4.4 CT Ratio Selection Guidelines	20

4.5 Comprehensive CT/PT Selection Matrix	20

Section 5: Communication & SCADA Integration	22

5.1 DNP3 Protocol Specifications	22

5.2 Modbus Protocol Specifications	22

5.3 IEC 61850 Metering Data Flows	23

5.4 Data Mapping and Integration Requirements	23

5.5 Cybersecurity Considerations	24

Section 6: Vendor Benchmarking	25

6.1 Itron	25

6.2 Landis+Gyr	25

6.3 Schneider Electric	26

6.4 GE (now Grid Solutions / Vernova)	26

6.5 Vendor Comparison Matrix	27

Section 7: Delta Metering Specification Package	28

7.1 Complete Technical Specification Template	28

7.1.1 Project Information Block	28

7.1.2 Current Transformer Specification	28

7.1.3 Potential Transformer (PT/VT) Specification	28

7.1.4 Revenue Meter Specification	29

7.2 Installation Requirements	29

7.3 Testing and Commissioning Procedures	30

7.3.1 Pre-Energization Tests	30

7.3.2 Energized Commissioning Tests	30

7.4 Quality Assurance Requirements	30

Section 8: Revenue-Leakage Prevention Checklist	32

8.1 Common Revenue Leakage Points	32

8.2 Prevention Strategies by Project Phase	33

8.2.1 Design Phase	33

8.2.2 Procurement Phase	33

8.2.3 Installation Phase	33

8.2.4 Commissioning Phase	34

8.2.5 Operations and Maintenance Phase	34

8.3 Verification Procedures	34

References	36

# Executive Summary

This Specification Package (S-UI-03) establishes the engineering baseline for revenue-grade utility metering and instrument transformer (CT/PT) systems deployed within Delta's East Coast microgrid integration program. It is the second deliverable in the S-UI series and draws directly on the technical research documented in the Delta Engineering IEEE 2030.7/2030.8 Microgrid Compliance Report for East Coast Utility Jurisdictions (June 2026).

Revenue-grade metering is the financial cornerstone of every grid-interactive microgrid project. From the moment of interconnection, the utility revenue meter and its associated instrument transformers constitute the legally defensible "cash register" for all energy settlement transactions, net metering credits, and demand charges. Errors, non-compliant installations, or inadequate accuracy class selection carry direct financial consequences—including rejected commissioning inspections, re-work costs, and delayed revenue commencement.

This package addresses the following key deliverables:

A structured review of governing standards: ANSI C12.1, C12.20, IEEE C57.13, and IEC 61869.

Regional metering rules for PJM, NYISO, ISO-NE, and MISO-East jurisdictions.

Utility-specific revenue meter and CT/PT specifications for ten major East Coast utilities.

A comprehensive CT/PT selection matrix covering MV applications at 15 kV and 35 kV.

Communication and SCADA integration requirements including DNP3, Modbus, and IEC 61850.

Vendor benchmarking for Itron, Landis+Gyr, Schneider Electric, and GE meters.

A Delta metering specification template and quality assurance procedures.

A revenue-leakage prevention checklist for use during design, installation, and commissioning.

The specification approach prioritizes strict conformance with utility metering manuals (e.g., ConEd MES-350, Eversource Yellow Book, PSE&G Transmission Interconnection Requirements) while providing Delta engineers with the engineering judgment framework required to navigate the site-specific variability inherent across ten different utility territories spanning six RTOs/ISOs.

# Section 1: Standards Review

Revenue-grade metering in the United States is governed by an interlocking framework of ANSI, IEEE, and IEC standards. Understanding their scope, accuracy class definitions, and compliance implications is essential for Delta engineers designing, procuring, and commissioning metering systems across East Coast utility jurisdictions.

## 1.1 ANSI C12.1 – Code for Electricity Metering

ANSI C12.1 is the foundational North American standard for electricity meters, establishing acceptable performance criteria for new electromechanical and solid-state meters. It prescribes test procedures for accuracy, stability, and environmental performance, and defines minimum requirements for meter design, marking, and installation. All utility-approved revenue meters deployed by East Coast utilities must be certified to this standard.

Key requirements under ANSI C12.1 include:

Accuracy maintained across a defined test current range (typically 10%–200% of test amperes).

Temperature performance from –40°C to +70°C for outdoor installations.

Dielectric withstand (voltage) testing at 2,500 V for one minute.

Mechanical endurance requirements for terminal connections and meter sockets.

Marking requirements: manufacturer, model, accuracy class, voltage, and current ratings on nameplate.

## 1.2 ANSI C12.20 – Accuracy Classes 0.2 and 0.5

ANSI C12.20 extends C12.1 by defining specific accuracy classes for high-accuracy solid-state electronic meters used for revenue settlement at commercial and industrial facilities, including microgrids. It defines two principal accuracy classes:

| Accuracy Class | Maximum Error at Full Load | Maximum Error at Light Load (10%) | Typical Application |
| --- | --- | --- | --- |
| 0.2 | ±0.2% | ±0.3% | Large commercial/industrial, utility-side revenue metering, transmission-level interconnections |
| 0.5 | ±0.5% | ±1.0% | Medium commercial, distribution-level interconnections, sub-metering where utility approves |

For microgrid and DER interconnections, utilities on the East Coast virtually universally require the 0.2 accuracy class. The 0.5 class may be acceptable for check metering or internal revenue purposes but should not be specified for the primary utility revenue meter without explicit written approval from the utility's metering engineering department.

## 1.3 IEEE C57.13 – Instrument Transformers

IEEE C57.13 is the primary US standard governing the performance, construction, and testing of current transformers (CTs) and voltage transformers (VTs/PTs). It is the definitive reference for selecting instrument transformers for revenue metering applications. All CTs and PTs installed at the utility revenue metering point must comply with this standard.

### 1.3.1 Accuracy Classes Under IEEE C57.13

The standard defines separate accuracy classes for metering and relaying service:

| Class | Max Ratio Correction Factor (RCF) Error | Max Phase Angle Error (min) | Valid Range | Application |
| --- | --- | --- | --- | --- |
| 0.15S | ±0.15% | ±8 min | 1%–120% rated current (S = extended range) | Revenue CT for renewable/variable sources; NYISO, ISO-NE preferred |
| 0.3S | ±0.30% | ±15 min | 1%–120% rated current | Revenue CT general purpose; widely accepted by PJM utilities |
| 0.3 | ±0.30% | ±15 min | 10%–120% rated current | Revenue CT, stable industrial load; not suitable for solar/wind |
| 0.6 | ±0.60% | ±30 min | 10%–120% rated current | Check metering; substation monitoring; not revenue grade at most utilities |
| 1.2 | ±1.20% | ±60 min | 10%–120% rated current | Relaying; protection only; never use for revenue measurement |
| 2.4 | ±2.40% | ±120 min | 10%–120% rated current | Relaying (coarse); protection backup; not for metering |

Important: The "S" suffix (e.g., 0.15S, 0.3S) indicates that the transformer maintains its rated accuracy class down to 1% of rated current, compared to 10% for non-S classes. This is critical for microgrids with solar PV or battery storage, which can operate at very low output levels. Utilities with high DER penetration (notably ConEd, NYISO territory, and ISO-NE) increasingly require the S designation.

### 1.3.2 Burden Ratings

The burden is the impedance of the secondary circuit (wiring + meter coils + relay coils) presented to the CT secondary. IEEE C57.13 defines standard burden designations. Exceeding the rated burden causes the CT to saturate, introducing significant ratio error and negating its accuracy rating.

| Burden Designation | Impedance (Ω) | VA at 5A | Power Factor | Application |
| --- | --- | --- | --- | --- |
| B-0.1 | 0.1 | 2.5 | 0.9 | Very short secondary leads; meter only |
| B-0.2 | 0.2 | 5.0 | 0.9 | Short secondary leads (<10 ft); meter + minimal wiring |
| B-0.5 | 0.5 | 12.5 | 0.9 | Medium leads (<25 ft); meter + relay; standard for most revenue installations |
| B-1.0 | 1.0 | 25.0 | 0.5 | Long leads (<50 ft); multiple instruments; calculate actual burden |
| B-2.0 | 2.0 | 50.0 | 0.5 | Extended runs; rarely used for revenue; calculate actual burden |

## 1.4 IEC 61869 – Instrument Transformers (International)

IEC 61869 is the international equivalent of IEEE C57.13 and is the governing standard in most non-North American markets. While East Coast utilities mandate IEEE C57.13 compliance, IEC 61869 defines comparable accuracy classes that are important for understanding internationally sourced equipment:

| IEC 61869 Class | IEEE C57.13 Equivalent | Max Ratio Error (%) | Application Context |
| --- | --- | --- | --- |
| 0.1 | Between 0.15S and 0.15 | ±0.10% | Precision laboratory / reference standard metering |
| 0.2S | ~0.15S | ±0.20% (down to 1% Irat) | Revenue metering, variable generation (international standard) |
| 0.5S | ~0.3S | ±0.50% (down to 1% Irat) | Revenue metering, general (international) |
| 0.2 | ~0.3 | ±0.20% (10%–120% range) | Revenue metering, stable industrial |
| 0.5 | ~0.6 | ±0.50% (10%–120% range) | Commercial metering |
| 1 | Class 1 / 0.6 | ±1.00% | Check metering |
| 3 | Relaying | ±3.00% | Protection relay service |
| 5P / 10P | C class relaying | Protection accuracy | Fault current measurement / relaying |

Delta engineers should note that some equipment vendors (particularly European manufacturers) provide IEC class designations. When procuring CTs/PTs for US East Coast utility revenue metering, always verify the vendor has obtained IEEE C57.13 certification and that the nameplate clearly shows the ANSI accuracy class.

## 1.5 IEC 62056 – DLMS/COSEM Data Exchange

IEC 62056 defines the Device Language Message Specification / Companion Specification for Energy Metering (DLMS/COSEM), a globally adopted standard for smart meter data exchange. It provides an object-oriented data model (COSEM) and a messaging protocol (DLMS) for reading, configuring, and managing meters over any network. Many modern ANSI C12.22 meters incorporate DLMS/COSEM as an additional communication layer, particularly for AMI back-office integration. Delta engineers should verify whether the target utility's AMI head-end supports DLMS/COSEM or requires native ANSI C12.22 framing.

# Section 2: Regional Metering Rules

Revenue metering requirements are shaped not only by equipment standards but also by the tariff structures, net metering rules, and interconnection procedures of each regional market. This section summarizes the metering-relevant rules for PJM, NYISO, ISO-NE, and MISO-East, with specific attention to billing structures, compensation mechanisms, and metering configuration requirements.

## 2.1 NYISO Territory

NYISO oversees wholesale electricity markets in New York State. Retail-level net metering is governed by the New York Public Service Commission (NY PSC) under Case 15-E-0751 and the Standardized Interconnection Requirements (SIR). Key metering requirements include:

Bi-directional metering: A single bi-directional revenue meter is the standard for net metering facilities.

Interval data: The meter must record 15-minute interval data for both import and export, accessible remotely by the utility.

Accuracy class: 0.2 meter accuracy required; 0.15S CTs preferred for variable DER.

IEEE 1547-2018 compliance: All DER equipment must comply; UL 1741-SB certification required.

Net Excess Generation (NEG): Compensated at the monthly avoided cost rate (wholesale); credited annually.

Non-bypassable charges: Certain delivery charges (e.g., Systems Benefits Charge, Renewable Portfolio Standard) are applied on a gross-consumption basis and are not offset by net metering credits.

Islanding detection: Unintentional islanding must be detected within 2 seconds (NYISO Default Settings).

## 2.2 ISO-NE Territory (CT, MA, ME, NH, RI, VT)

ISO-NE operates the wholesale market and transmission system for New England. Retail metering and net metering are governed by individual state commissions:

Massachusetts (MA): Net metering at retail rate; Class I (≤60 kW), Class II (61 kW–1 MW), Class III (>1 MW). Export credits apply at retail rate for Class I/II; Class III subject to competitive procurement.

Connecticut (CT): Virtual net metering available. Eversource and UI administer; export credit at retail avoided cost rate.

New Hampshire (NH): Limited net metering program; Eversource requirement for primary metering approvals.

Meter requirement: Revenue-grade bi-directional meter; 15-minute interval data; remote AMI communication.

CT/PT requirement: IEEE C57.13 accuracy class 0.3S or better; burden calculations required and submitted to utility metering engineering.

ISO-NE SRD 2018: Revenue metering must be in place before commercial operation date (COD). Metering data used for settlement in ISO-NE markets.

## 2.3 PJM Territory (DE, MD, NJ, PA, VA, NC, WV, IL, IN, OH, MI)

PJM is the largest RTO in the US and covers significant portions of the East Coast. Net metering rules are set by individual state PUCs, but PJM imposes uniform requirements on wholesale market participants:

Revenue metering: PJM requires ANSI C12.20 class 0.2 meters for all market-participating resources.

Telemetry: Real-time output data must be submitted to PJM via Electronic Data Interchange (EDI) or dedicated telemetry. Meter data used in PJM settlement.

New Jersey (PSE&G territory): Retail-rate net metering credits; annualized true-up with excess compensated at LMP (locational marginal price) rate.

Maryland (BGE territory): Net metering up to system size equal to customer load; excess generation rolled over monthly; annual cash-out at wholesale rate.

Pennsylvania (PPL territory): Net metering capped at customer load; bi-directional meter required; excess generation credited at wholesale avoided cost.

Virginia/NC (Dominion territory): Net metering governed by VA/NC commissions; export at retail rate up to 12-month rolling bank; excess paid at avoided cost.

PJM Manual 14G: Outlines metering requirements for generation facilities interconnecting at transmission level; redundant revenue metering may be required.

## 2.4 MISO-East Territory (MI, IN, MN, IA)

MISO-East covers the Midwest, including DTE Energy territory in Michigan and Commonwealth Edison (ComEd) in Illinois. Net metering rules vary by state:

Michigan (DTE Energy): Net metering program capped at 1% of prior year peak; bi-directional meter required; retail rate credit up to system size.

Illinois (ComEd): Illinois Net Metering Law (P.A. 102-0662) provides for net metering at retail rate; ComEd administers the program.

Meter requirements: ANSI C12.20 compliant; 15-minute interval recording; AMI communication (cellular or RF mesh).

MISO tariff: For wholesale market participants, MISO settlement requires certified revenue metering with direct telemetry to MISO.

## 2.5 Regional Metering Summary Matrix

| RTO/ISO | State(s) | Net Metering Compensation | Interval Data Required | Preferred CT/PT Class | Key Metering Standard |
| --- | --- | --- | --- | --- | --- |
| NYISO | NY | NEG at wholesale avoided cost | 15-min import + export | 0.15S | ANSI C12.20 Class 0.2 |
| ISO-NE | MA, CT | Retail rate (Class I/II); Competitive (Class III) | 15-min | 0.3S or 0.15S | ANSI C12.20 Class 0.2 |
| ISO-NE | NH, RI, VT, ME | Retail rate (program caps apply) | 15-min | 0.3S | ANSI C12.20 Class 0.2 |
| PJM | NJ | Retail rate; annual LMP true-up | 15-min | 0.3S | ANSI C12.20 Class 0.2 |
| PJM | MD, PA | Retail rate; annual wholesale true-up | 15-min | 0.3S | ANSI C12.20 Class 0.2 |
| PJM | VA, NC | Retail rate; 12-month rolling bank | 15-min | 0.3 | ANSI C12.20 Class 0.2 |
| MISO-East | MI | Retail rate (program cap) | 15-min | 0.3S | ANSI C12.20 Class 0.2 |
| MISO-East | IL | Retail rate (P.A. 102-0662) | 15-min | 0.3S | ANSI C12.20 Class 0.2 |

# Section 3: Utility Revenue Meter Specifications

Each East Coast utility maintains an approved meter list and detailed metering manuals that govern the specific meter models, CT/PT specifications, installation requirements, and communication protocols acceptable for revenue service. This section provides the engineering-level specifications for ten target utilities, derived from official utility documents including ConEd MES-350, Eversource Yellow Book, PSE&G Transmission Interconnection Requirements, and Dominion Interconnection Parameters.

## 3.1 Con Edison (ConEd) – New York City and Westchester

Governing Documents: Electric Service Reference Manual ("Blue Book") Section VII; MES-350 (HT Metering). [Refs 48, 49]

Meter Type: Revenue meters are ConEd-furnished for secondary service; primary (HT) metering requires customer-furnished metering cabinet with ConEd-furnished CTs/PTs.

Meter Models: Approved models per ConEd current approved vendor list (typically Itron or Landis+Gyr solid-state).

CT/PT Ownership: ConEd furnishes instrument transformers; customer provides and installs the metering cabinet, conduit, and secondary wiring.

CT/PT Accuracy: 0.15S (preferred for variable DER); 0.3S minimum.

Secondary Wiring: #10 AWG stranded copper, continuous without splices, in dedicated conduit. Maximum 25-foot distance from transformers to meter.

Metering Location: Accessible outdoors at grade level; meter center 4 ft 6 in. to 5 ft 6 in. above finished grade.

Drawing Approval: All metering installation drawings require prior ConEd approval from Metering Engineering before construction.

Bi-directional: Required for all net metering and export-capable installations.

Communication: AMI cellular or RF as required by ConEd AMI program; customer does not provide communication infrastructure.

No CT fusing: CT secondary circuits must remain closed at all times; no fuses, switches, or overcurrent devices permitted in CT secondary circuit.

Network Grid Export: Installations on ConEd secondary network grid require Communications Aided Tripping (CAT) scheme; SCADA mandatory.

## 3.2 National Grid – New York, Massachusetts, Rhode Island

Governing Documents: ESB 756; MA M.D.P.U. No. 1468 DG Interconnection Tariff; RI Tariff. [Refs 28, 30]

Meter Type: Utility-owned, solid-state electronic, bi-directional ANSI C12.20 Class 0.2.

Metering Configuration: Determined per interconnection study; primary metering required for MV interconnections.

CT/PT: Customer installs utility-approved instrument transformers; settings and ratio approved by National Grid Metering Engineering.

Accuracy Class: Per IEEE C57.13; 0.3 minimum, 0.3S for variable generation.

Setting Control: All relay and metering settings (including CT ratios and burden calculations) are subject to National Grid written approval; may not be modified without written consent.

Meter Location: Must provide 24/7 access for utility personnel; key-lockable enclosure.

Communication: ANSI C12.22 over cellular or RF; interval data transmitted to National Grid AMI head-end.

State Variations: NY SIR governs timing and categories; MA tariff may require additional monitoring for reliability.

## 3.3 Eversource – Connecticut, Massachusetts, New Hampshire

Governing Documents: Requirements for Electric Service ("Yellow Book") [NB-3]; Rules and Regulations for Electric Service. [Refs 50, 51]

Meter Type: Utility owns and installs meter; customer installs utility-approved CTs/VTs.

Primary Metering: Requires specific written approval from Meter Engineering; customer pays cost difference (CIAC) vs. secondary metering.

CT Polarity: H1 white-dot terminal must face line/utility side; H2 faces load; wiring to be verified during commissioning.

CT Accuracy: IEEE C57.13; 0.3S class required for all renewable and variable-output generation.

Installation: All metering must be outdoors unless variance granted; 4-foot wide x 3-foot deep clearance required in front of meters.

Communication: Remote communication (interval data) requires customer-provided dedicated analog phone line or approved equivalent near the meter location. Cellular modem acceptable with Eversource approval.

Billing: Traditional and Virtual Net Metering available; export credits at retail rate up to program caps.

Drawing Submission: Metering one-line and installation drawings must be submitted with interconnection application.

## 3.4 Duke Energy – North Carolina, South Carolina, Florida

Governing Documents: Duke Interconnection Procedures; ISOP Framework. [Refs 32, 33]

Meter Type: Duke-owned or customer-provided per interconnection agreement; solid-state electronic ANSI C12.20.

Configuration: Requirements determined through formal Duke interconnection study process; no single prescriptive document.

CT/PT: IEEE C57.13 compliant; accuracy class per Duke Metering Engineering specification issued during study.

SCADA/Telemetry: For commercial-scale interconnections, Duke requires real-time monitoring integrated with National Operations Control Center (NOC); communication via cellular or fiber.

Net Metering (NC/SC): State-specific programs; bi-directional meter required; annual true-up.

Commissioning: Duke witnesses commissioning test; metering certification must be provided.

## 3.5 Dominion Energy – Virginia, North Carolina

Governing Documents: Interconnection Parameters for DER Manual; Facility Interconnection Requirements. [Refs 35, 36]

Meter Type: ANSI C12.20 Class 0.2; solid-state electronic; bi-directional for net metering facilities.

CT/PT: IEEE C57.13 and ANSI C12 compliant; accuracy class specified per facility size and type.

Redundant Metering: Required for larger distribution and all transmission-level interconnections.

Disconnect: Lockable, utility-accessible disconnect switch on customer side of meter is mandatory.

UL 1741: All grid-tie equipment (inverters, energy storage) must be UL 1741 compliant.

Communication: Real-time data exchange to Dominion control center for larger facilities; cellular or fiber backhaul.

DTT Integration: For facilities requiring Direct Transfer Trip, SCADA and redundant revenue metering are co-located at POI.

## 3.6 DTE Energy – Michigan

Governing Documents: Michigan Public Service Commission Rules; MISO Interconnection Requirements.

Meter Type: ANSI C12.20; bi-directional; AMI-capable with cellular communication.

Net Metering Cap: Program capped at 1% of prior year system peak; meter programming must prevent billing of backfed energy until program enrollment confirmed.

CT/PT: IEEE C57.13 Class 0.3S for variable sources; burden calculations required.

AMI: DTE AMI network; cellular modem required at meter location; customer ensures adequate signal.

## 3.7 ComEd – Illinois

Governing Documents: Illinois Commerce Commission Rules; P.A. 102-0662; MISO Tariff.

Meter Type: ANSI C12.20 Class 0.2; ComEd-owned AMI meter for residential/small commercial; commercial-scale may require separate revenue-grade primary meter.

Net Metering: P.A. 102-0662 provides retail-rate net metering; bi-directional metering required; annual true-up.

CT/PT: IEEE C57.13; accuracy class per ComEd Metering Engineering approval.

Communication: ComEd AMI network; 15-minute interval data transmitted automatically.

## 3.8 PSE&G – New Jersey

Governing Documents: Transmission Interconnection Requirements (Doc. 063436); NJ BPU Net Metering Rules. [Refs 52, 53]

Meter Ownership: PSE&G owns revenue meter for transmission-level interconnections; customer provides/installs CT/PT units subject to utility approval and witness testing.

MV Metering (34.5 kV+): Walk-in metering enclosure required with auxiliary power and lighting.

CT/PT Distance: Maximum 100-foot distance between CT/PTs and meter; dedicated underground conduit required.

Grounding: Single point ground for CT/PT secondary neutral; multiple grounds strictly prohibited.

Accuracy: IEEE C57.13 metering-class CTs/PTs must not be used for relaying (use separate relaying-class CTs).

No Fusing: CT secondary circuits must not have fuses or bypass switches.

Cellular Signal: Customer must ensure adequate cellular signal strength at meter site for remote data acquisition by PSE&G.

Net Metering Compensation: Retail-rate credits; annualized true-up; excess at LMP wholesale rate. [Ref 53]

## 3.9 BGE – Maryland

Governing Documents: Maryland PSC Net Metering Rules; PJM Manual 14G guidance.

Meter Type: ANSI C12.20 Class 0.2; bi-directional AMI meter.

Net Metering: Retail rate credit up to system load size; monthly carryover; annual cash-out at wholesale avoided cost.

CT/PT: IEEE C57.13 Class 0.3S; accuracy calculations and drawings required at interconnection application.

Communication: BGE AMI network; 15-minute interval data.

## 3.10 PPL – Pennsylvania

Governing Documents: Pennsylvania PUC Net Metering Regulations; PPL Interconnection Manual; PJM Manual 14G.

Meter Type: ANSI C12.20 Class 0.2; bi-directional.

Net Metering: Retail rate credits; bi-directional meter; excess energy credited at avoided cost rate annually.

CT/PT: IEEE C57.13; 0.3S for renewables; burden and polarity verification required during commissioning.

Communication: PPL AMI network or customer-provided cellular modem per PPL specification.

## 3.11 Utility Revenue Meter Requirements Summary Matrix

| Utility | Meter Owner | Min Accuracy Class | CT/PT Owner | Min CT Class | Max CT-Meter Distance | Communication |
| --- | --- | --- | --- | --- | --- | --- |
| ConEd | ConEd | C12.20 / 0.2 | ConEd furnishes | 0.15S | 25 ft | AMI (ConEd network) |
| National Grid | Utility | C12.20 / 0.2 | Customer (utility approved) | 0.3S | Per study | ANSI C12.22/cellular |
| Eversource | Utility | C12.20 / 0.2 | Customer (utility approved) | 0.3S | Per Yellow Book | Cellular/phone line |
| Duke Energy | Per study | C12.20 / 0.2 | Per study | Per study | Per study | Cellular/fiber |
| Dominion | Per agreement | C12.20 / 0.2 | Customer/utility per study | 0.3 | Per study | Cellular/fiber |
| DTE | DTE | C12.20 / 0.2 | Customer (utility approved) | 0.3S | Per manual | AMI cellular |
| ComEd | ComEd | C12.20 / 0.2 | Customer (utility approved) | 0.3S | Per manual | AMI (ComEd network) |
| PSE&G | PSE&G | C12.20 / 0.2 | Customer (utility approved) | 0.3S | 100 ft | AMI cellular |
| BGE | BGE | C12.20 / 0.2 | Customer (utility approved) | 0.3S | Per manual | AMI cellular |
| PPL | PPL | C12.20 / 0.2 | Customer (utility approved) | 0.3S | Per manual | AMI cellular |

# Section 4: CT/PT Selection Matrix

Correct instrument transformer selection is one of the most technically demanding aspects of revenue metering design. An improperly selected or installed CT/PT can result in persistent billing errors, failed utility acceptance tests, and costly re-work. This section provides Delta engineers with a systematic framework for CT/PT selection, burden calculation, and ratio selection for all common East Coast microgrid applications.

## 4.1 MV Applications – 15 kV Class

Microgrids interconnecting at 13.8 kV or 15 kV (nominal) are the most common MV application on the East Coast distribution grid. The following specifications apply:

| Parameter | Specification | Notes / Basis |
| --- | --- | --- |
| Primary Voltage Class | 15 kV | IEEE C57.13 insulation level; covers 13.2 kV, 13.8 kV, 14.4 kV systems |
| PT Ratio | 14,400:120 V (120:1) | Most common; verify actual system voltage with utility |
| PT Accuracy Class | 0.3 (metering); 1.2Y (relaying) | Dual-wound or dual-core; metering core separate from relaying core |
| PT Secondary VA | 75–200 VA per phase | Size per actual secondary burden; allow 2× safety margin |
| CT Primary Range | 50–4,000 A (application-specific) | Select ratio so 100% load = ~75–80% of CT primary rating |
| CT Accuracy Class (Revenue) | 0.15S (preferred) / 0.3S (minimum) | "S" class required for renewable DER; verify with utility metering engineer |
| CT Secondary | 5 A (standard) | Some utilities accept 1 A secondary; verify with utility before specifying |
| CT Thermal Rating (Continuous) | 100% of rated; 150% continuous-rated preferred | Microgrid export can exceed import; specify for max bidirectional current |
| CT Fault Rating (Short-time) | ≥20× IN for 1 second (minimum) | Calculate maximum available fault current at POI; verify CT withstand |
| CT Accuracy Burden | B-0.5 or B-1.0 | Select based on calculated secondary circuit impedance |
| Wiring Standard | #10 AWG Cu, continuous, in dedicated conduit | ANSI/utility requirement; no splices, no other circuits in conduit |
| CT-to-Meter Distance | 25 ft (ConEd); 100 ft (PSE&G); per utility | Use maximum distance specified in utility metering manual |
| Secondary Grounding | Single-point ground at CT secondary neutral | Never ground at multiple points; use dedicated ground conductor |
| CT Secondary Protection | NONE (no fuses, no switches) | Open CT secondary is lethal hazard; shorting terminal blocks for maintenance |

## 4.2 MV Applications – 35 kV Class

Microgrids interconnecting at 34.5 kV (PSE&G transmission, Dominion) or 35 kV class systems have additional insulation and fault current considerations:

| Parameter | Specification | Notes / Basis |
| --- | --- | --- |
| Primary Voltage Class | 35 kV | IEEE C57.13; covers 34.5 kV, 33 kV systems |
| PT Ratio | 34,500:120 V (287.5:1) | Standard; verify actual voltage with utility |
| PT Accuracy Class | 0.3 (metering); 1.2Y (relaying) | Dual-core; metering and relaying cores must be physically separate |
| CT Primary Range | 100–6,000 A (application-specific) | Select ratio for max import/export current at 100% rated output |
| CT Accuracy Class | 0.15S (for variable DER) / 0.3S (general) | PSE&G, Dominion mandate 0.3S minimum at 34.5 kV |
| CT Short-time Rating | ≥25× IN for 1 second | 34.5 kV systems typically have higher fault levels; verify with utility SCC |
| CT Continuous Thermal Rating | 1.0 continuous; 1.5 preferred for bidirectional | Account for full microgrid export capacity |
| Walk-in Metering House | Required by PSE&G at 34.5 kV | Auxiliary lighting and power required per PSE&G Doc. 063436 |
| Wiring | #10 AWG Cu, dedicated underground conduit | Underground conduit between outdoor CT/PT cabinet and indoor meter |
| Max CT-Meter Distance | 100 ft (PSE&G); per utility for others | Calculate burden at maximum specified distance; verify against CT burden rating |

## 4.3 Burden Calculations

The CT burden is the total impedance of the secondary circuit, including:  (1) CT secondary wiring resistance, (2) meter current coil impedance, (3) relay coil impedance (if relaying CTs are combined — NOT recommended for revenue), and (4) terminal/connector resistance. The total burden must not exceed the CT's rated burden at the specified accuracy class.

Burden Calculation Formula:

Z_total = Z_wire + Z_meter_coil + Z_relay_coil + Z_terminals

Z_wire = 2 × ρ × L / A  [where ρ = copper resistivity 1.72×10⁻⁸ Ω·m; L = one-way lead length (m); A = conductor cross-sectional area (m²)]

For #10 AWG Cu (5.26 mm²): Z_wire per 100 ft (one-way) ≈ 0.062 Ω at 20°C; multiply by 2 for two-wire circuit

Typical revenue meter current coil impedance: 0.01–0.10 Ω (verify with manufacturer datasheet)

Example Burden Calculation (15 kV, 50 ft CT-to-meter distance, #10 AWG):

| Component | Impedance (Ω) | Notes |
| --- | --- | --- |
| CT wiring (50 ft one-way, #10 AWG) | 0.062 Ω | 2 × 0.031 Ω/100 ft × 100 ft total loop |
| Revenue meter coil (Itron, typical) | 0.048 Ω | Per Itron meter datasheet |
| Terminal blocks + connectors | 0.010 Ω | Estimated; verify with actual hardware |
| Total Secondary Burden | 0.120 Ω | Must be < CT rated burden (B-0.2 = 0.2 Ω; B-0.5 = 0.5 Ω) |
| Result | Acceptable for B-0.2 and B-0.5 | Use B-0.5 rated CT; safety margin confirmed |

## 4.4 CT Ratio Selection Guidelines

The CT ratio must be chosen so that the full range of the microgrid's expected import and export current falls within the CT's accurate operating range. The following guidelines apply:

Target Design Point: Select CT primary so that maximum expected current equals approximately 75–80% of CT primary rating. This provides safety margin while keeping secondary current in the accurate upper range.

Extended Range ("S" class): If the facility will regularly operate below 10% of CT primary (e.g., overnight solar facility with minimal standby load), specify 0.15S or 0.3S class to ensure accuracy at low currents.

Bidirectional Operation: For microgrids with net export capability, the CT must be sized for the maximum of either import or export current. Use the same CT for both directions; bi-directional meters handle the sign convention in firmware.

Standard Ratios: Use standard ANSI ratios (e.g., 200:5, 400:5, 600:5, 800:5, 1200:5, 2000:5). Non-standard ratios require utility approval and may have longer procurement lead times.

Tap Selectable CTs: Some utilities permit multi-ratio CTs with selectable taps (e.g., 600:5/300:5/200:5). Confirm with utility metering engineer before specifying.

## 4.5 Comprehensive CT/PT Selection Matrix

| Application | System Voltage | Typical Load Range (A) | Recommended CT Ratio | CT Accuracy Class | PT Ratio | PT Class | Max Burden (CT) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Small commercial DER (<250 kW) | 13.8 kV | 10–100 A | 100:5 | 0.3S | 13,800:120 (115:1) | 0.3 | B-0.2 |
| Medium commercial DER (250–1,000 kW) | 13.8 kV | 15–250 A | 200:5 or 300:5 | 0.3S | 13,800:120 | 0.3 | B-0.5 |
| Large commercial / microgrid (1–5 MW) | 13.8 kV | 50–650 A | 600:5 or 800:5 | 0.15S | 13,800:120 | 0.3 | B-0.5 |
| Utility-scale microgrid (5–20 MW) | 13.8 kV | 200–3,000 A | 2000:5 or 3000:5 | 0.15S | 13,800:120 | 0.3 | B-1.0 |
| Medium commercial (34.5 kV) | 34.5 kV | 10–200 A | 200:5 or 400:5 | 0.3S | 34,500:120 | 0.3 | B-0.5 |
| Large commercial / microgrid (34.5 kV) | 34.5 kV | 50–1,200 A | 800:5 or 1200:5 | 0.15S | 34,500:120 | 0.3 | B-1.0 |
| Utility-scale (34.5 kV, 20+ MW) | 34.5 kV | 300–4,000 A | 2000:5 or 4000:5 | 0.15S | 34,500:120 | 0.3 | B-1.0 |
| Revenue check meter (secondary) | 480 V | 100–2,000 A | Calculated per load | 0.3S | Direct (480 V input) | N/A | B-0.5 |

# Section 5: Communication & SCADA Integration

Revenue meters in modern grid-interactive microgrid installations are not passive recorders — they are active nodes in a utility's Advanced Metering Infrastructure (AMI), SCADA, and billing systems. Correct implementation of communication protocols is a hard acceptance criterion for interconnection. This section specifies DNP3, Modbus, and IEC 61850 integration requirements along with relevant cybersecurity considerations.

## 5.1 DNP3 Protocol Specifications

DNP3 (Distributed Network Protocol Version 3) is the dominant communication protocol for utility SCADA integration of field devices on the East Coast. Eversource, Dominion, PJM, and most other East Coast utilities require DNP3 for DER telemetry and revenue meter data acquisition:

| DNP3 Parameter | Specification | Notes |
| --- | --- | --- |
| Standard | IEEE Std 1815-2012 (DNP3) | DNP3 Level 2 compliance minimum; Level 3 for advanced functions |
| Transport | TCP/IP (primary); serial RS-232/RS-485 (legacy) | TCP port 20000 (default); utility may specify alternate port |
| Polling Mode | Unsolicited reporting + polled (dual mode) | Eversource DER Gateway uses unsolicited class 1/2/3 reporting |
| Data Objects (Metering) | Analog Input (Group 30); Counter (Group 20/22) | Real power (W), Reactive power (VAR), Energy (Wh, VARh), Voltage, Current |
| Data Objects (Status) | Binary Input (Group 1); Control Output (Group 12) | Breaker status, DER run/stop, export enable/disable |
| Integrity Poll Interval | ≤15 minutes | Ensures meter data consistency; utility may require shorter intervals |
| Event Reporting | Class 1 (high priority), Class 2/3 (lower) | Breaker operations and alarms: Class 1; Analog changes: Class 2 |
| Authentication | DNP3 SAv5 (Secure Authentication Version 5) | Mandatory for new installations per NERC CIP and utility cybersec policy |
| RTU Integration | SEL-3530 or equivalent DNP3-capable RTU | RTU polls meter via DNP3; RTU communicates to utility EMS/SCADA |
| Data Latency | ≤4 seconds for control commands; ≤60 sec for metering | Utility-specified; verify during commissioning with utility SCADA |

## 5.2 Modbus Protocol Specifications

Modbus TCP/RTU is widely used for internal microgrid data acquisition — between the energy management system (EMS) and individual DER controllers, sub-meters, and monitoring devices. While utilities rarely accept Modbus as the primary SCADA protocol, it is the de facto standard for EMS-to-device communication:

| Modbus Parameter | Specification | Notes |
| --- | --- | --- |
| Standard | Modbus Application Protocol V1.1b3 | Modbus TCP (Ethernet) preferred; RTU over RS-485 for legacy devices |
| TCP Port | 502 (standard) | Do not change without updating EMS configuration |
| Register Map | IEEE 1815 / Sunspec Alliance Modbus Registers (preferred) | Sunspec provides standardized register maps for DER; reduces integration effort |
| Typical Metering Registers | Watts (Int32), VARs (Int32), Wh (Int32), V (Int16), A (Int16) | Exact register addresses per meter/device manufacturer datasheet |
| Poll Rate | 1–10 seconds (operational data); 1 minute (revenue data) | Faster polling for DER control; slower for energy accounting |
| Data Type | Big-Endian (Modbus standard) | Verify with device; some meters use Little-Endian; causes incorrect readings |
| Master/Slave | EMS = Master; meters/inverters = Slave | One master per Modbus segment; use gateway for multiple masters |
| Security Note | No authentication/encryption in standard Modbus | Use network-level security (VLAN, firewall) to isolate Modbus segments |

## 5.3 IEC 61850 Metering Data Flows

IEC 61850 is the international standard for substation automation and protection. As microgrids increase in complexity, IEC 61850 is gaining adoption as the communication backbone for DER integration, particularly in ISO-NE and NYISO territories where utilities are advancing Smart Grid architectures:

| IEC 61850 Element | Description | Metering Application |
| --- | --- | --- |
| MMXU (Measurement) | Three-phase power and energy measurements | Primary metering LN; maps to revenue meter data objects |
| MMTR (Metering) | Accumulated energy counters (Wh, VARh) | Billing-quality energy totals; interval data |
| MSQI (Sequence) | Positive, negative, zero sequence quantities | Power quality and unbalance monitoring |
| XCBR (Circuit Breaker) | POI breaker position and control | Status and trip/close commands via IEC 61850 GOOSE |
| CSWI (Switch Control) | Switch operation for isolation devices | Disconnect switch status reporting |
| GAPC (Generic Function) | Customizable function blocks | Utility-specific data objects not covered by standard LNs |
| GOOSE (Generic Object) | Fast binary messaging (<4 ms latency) | Protection trip signals; breaker status; not for revenue metering |
| Sampled Values (SV) | High-rate digitized current and voltage samples | Advanced power quality; merging unit interface; not for revenue billing |
| MMS (Manufacturing Msg) | Client-server data exchange over TCP/IP | Primary protocol for reading metering data from IEC 61850 IEDs |

For Delta EMS integration: When connecting to an IEC 61850 substation IED (e.g., a revenue meter with 61850 interface), use an IEC 61850 client library (e.g., libIEC61850 or a commercial SCADA server with 61850 support). Map MMXU and MMTR logical nodes to the EMS data points. Do not substitute DNP3 data for IEC 61850 data in utilities that have specified 61850 as the metering interface.

## 5.4 Data Mapping and Integration Requirements

The following minimum data points must be mapped and available via the primary utility SCADA/AMI interface for all East Coast revenue metering installations:

| Data Point | Units | Protocol Object (DNP3) | Protocol Object (IEC 61850) | Update Rate |
| --- | --- | --- | --- | --- |
| Real Power Import | kW | Group 30 Var2, Index 1 | MMXU.TotW | ≤1 min |
| Real Power Export | kW | Group 30 Var2, Index 2 | MMXU.TotW (negative) | ≤1 min |
| Reactive Power Import | kVAR | Group 30 Var2, Index 3 | MMXU.TotVAr | ≤1 min |
| Reactive Power Export | kVAR | Group 30 Var2, Index 4 | MMXU.TotVAr (negative) | ≤1 min |
| Active Energy Import | kWh | Group 22 Var5, Index 1 | MMTR.TotWh | 15-min interval |
| Active Energy Export | kWh | Group 22 Var5, Index 2 | MMTR.TotWh (export) | 15-min interval |
| Phase A/B/C Voltage | V | Group 30 Var2, Index 5–7 | MMXU.PhV.phsA/.phsB/.phsC | ≤1 min |
| Phase A/B/C Current | A | Group 30 Var2, Index 8–10 | MMXU.A.phsA/.phsB/.phsC | ≤1 min |
| Power Factor (Total) | pu | Group 30 Var2, Index 11 | MMXU.TotPF | ≤1 min |
| POI Breaker Status | Open/Closed | Group 1 Var2, Index 0 | XCBR.Pos.stVal | On change |
| Meter Tamper Alarm | Alarm | Group 2 Var2, Index 0 | GAPC.Ind | On event |
| Demand (15-min peak) | kW | Group 30 Var2, Index 12 | MMTR.DmdW | 15-min |

## 5.5 Cybersecurity Considerations

The integration of revenue meters and SCADA systems into IP networks creates cybersecurity obligations that are increasingly enforced by utilities and mandated by NERC CIP (Critical Infrastructure Protection) standards for larger facilities:

Network Segmentation: Revenue metering communication circuits must be on a dedicated, isolated VLAN or physical network segment separate from IT networks and building management systems.

Firewall Rules: Allow only required protocols and ports (e.g., TCP/20000 for DNP3; TCP/102 for IEC 61850 MMS). Block all other inbound and outbound traffic.

DNP3 Secure Authentication: Implement DNP3 SAv5 for all utility-facing DNP3 sessions. Do not use unauthenticated DNP3 for new installations.

Access Control: Role-based access for meter configuration; all configuration changes logged with timestamp and user ID.

Physical Security: Meter enclosures must be key-lockable; tamper-evident seals on terminal blocks; alarm on door opening.

Firmware Updates: Meter firmware updates must be performed by the utility or under utility supervision; document each update with version number and date.

NERC CIP Applicability: Facilities ≥20 MW connected to the BES may be subject to NERC CIP-002 through CIP-014; confirm applicability with utility and NERC regional entity.

# Section 6: Vendor Benchmarking

Delta engineers must select revenue meters exclusively from each utility's approved meter list. However, understanding the capabilities, models, and communication options of major vendors enables Delta to specify the correct model during the interconnection application and ensures compatibility with the utility AMI infrastructure. The following benchmarking covers the four dominant vendors on the East Coast market.

## 6.1 Itron

Company Profile: Itron is one of the two largest AMI system providers in the US. Widely deployed by ConEd, Eversource, and several PJM utilities. Strong in both meter hardware and AMI head-end software (OpenWay Riva network).

Key Revenue Meter Models:

Itron CENTRON II: Solid-state, single-phase/polyphase; ANSI C12.20 Class 0.2; bi-directional; widely used for commercial net metering in ConEd and ISO-NE territories.

Itron S4x Series (S4e, S4x): High-accuracy polyphase revenue meters; C12.20 Class 0.2; supports primary metering (external CTs/PTs); TCP/IP + ANSI C12.22 + optical port. Widely used for MV commercial and industrial accounts.

Itron OpenWay Riva: Smart endpoint platform; cellular LTE + mesh RF; ANSI C12.22 native; head-end integration via OpenWay collection engine.

Communication: ANSI C12.22 over cellular LTE (primary), 900 MHz RF mesh (secondary), optical port (local). DNP3 optional via add-on module.

East Coast Deployments: Widely deployed across ConEd (New York), Eversource (CT, MA), National Grid (RI). Standard meter for commercial/industrial AMI programs in these territories.

Power Quality: Optional IQ module for harmonics measurement (IEEE 519); demand recording; interval data (1–60 min configurable).

Delta Note: Confirm model and communication module specification with utility metering engineering before procurement. ConEd may specify exact firmware version.

## 6.2 Landis+Gyr

Company Profile: Landis+Gyr (L+G) is the other dominant global meter vendor, strong across both residential AMI and high-accuracy grid/industrial metering. Gridstream network for AMI head-end.

Key Revenue Meter Models:

L+G E650 Series: Flagship commercial/industrial revenue meter; ANSI C12.20 Class 0.2; polyphase; supports primary metering with external CTs/PTs; multi-function power quality; DNP3, Modbus, ANSI C12.22 communication options.

L+G FOCUS AXR: High-accuracy solid-state; used for large commercial/sub-transmission metering; optical port + advanced AMI modules.

L+G GRID360 / E360: Next-generation smart meter platform; 4G LTE cellular; advanced cybersecurity; TLS 1.2/1.3 encrypted communications.

Communication: Gridstream RF (900 MHz); LTE cellular; ANSI C12.22; optical port; DNP3 via module; IEC 62056/DLMS available.

Accuracy and Metrology: Landis+Gyr meters are known for exceptionally stable accuracy over temperature; E650 achieves 0.2% accuracy across –40°C to +70°C.

East Coast Presence: Strong presence with National Grid (MA, NY), PSE&G (NJ), and BGE (MD).

Delta Note: L+G E650 is the preferred specification for PSE&G and BGE primary metering applications due to its walk-in enclosure compatibility and strong utility acceptance record.

## 6.3 Schneider Electric

Company Profile: Schneider Electric provides metering through its PowerLogic product line, oriented toward facility energy management as well as utility revenue metering. Tightly integrated with EcoStruxure SCADA/EMS platform.

Key Revenue Meter Models:

PowerLogic ION9000: Utility-grade revenue meter; ANSI C12.20 Class 0.2; Class 0.1 energy accuracy (exceeds C12.20); extensive power quality (IEC 61000-4-30 Class A); DNP3, Modbus TCP, IEC 61850 native; LTE/cellular.

PowerLogic ION8650: Established utility revenue meter; ANSI C12.20; Modbus, DNP3, ANSI C12.22; used for commercial/industrial primary metering.

PowerLogic PM8000 Series: Advanced power quality meter; not typically a utility revenue meter but used for owner-side operational metering and power quality compliance.

Communication: Ethernet TCP/IP; Modbus TCP; DNP3; IEC 61850 (ION9000); ANSI C12.22; optical port. EcoStruxure integration.

Power Quality: Schneider meters are known for comprehensive power quality analysis; waveform capture; harmonic analysis to 511th harmonic; event logging.

Delta Application: The ION9000 is particularly well-suited for Delta EMS integration due to native IEC 61850 and DNP3 support. Verify utility approval before specifying for revenue service.

## 6.4 GE (now Grid Solutions / Vernova)

Company Profile: GE's Grid Solutions division (rebranded as GE Vernova) provides advanced meters primarily for transmission and wholesale market settlement. Less common for distribution-level net metering.

Key Revenue Meter Models:

GE KV2c: High-accuracy polyphase revenue meter; ANSI C12.20 Class 0.2; used for large commercial/industrial and wholesale settlement; DNP3 + ANSI C12.22 + optical port.

GE I-210+c: AMI-enabled residential/small commercial; less relevant for microgrid POI metering.

GE EPM 9450: Power quality and revenue meter; ANSI C12.20; multi-function; wide application in industrial and utility substation monitoring.

Communication: ANSI C12.22; DNP3; Modbus TCP; optical port; cellular via add-on module.

Application Notes: GE meters are well-suited for wholesale market settlement and transmission-level metering. For distribution-level microgrid interconnections, verify utility approval status as GE meters are less commonly on approved lists for retail AMI programs.

## 6.5 Vendor Comparison Matrix

| Criterion | Itron | Landis+Gyr | Schneider Electric | GE / Vernova |
| --- | --- | --- | --- | --- |
| ANSI C12.20 Accuracy | Class 0.2 ✓ | Class 0.2 ✓ | Class 0.2 / 0.1 ✓ | Class 0.2 ✓ |
| Primary Metering (CT/PT) | Yes (S4x) | Yes (E650) | Yes (ION9000) | Yes (KV2c) |
| Bi-directional | Yes ✓ | Yes ✓ | Yes ✓ | Yes ✓ |
| ANSI C12.22 (AMI) | Yes – native | Yes – native | Yes – module | Yes – module |
| DNP3 | Optional module | Optional module | Native (ION9000) | Native (KV2c) |
| IEC 61850 | Limited | Limited | Native (ION9000) | Limited |
| Modbus TCP | Optional | Optional | Native | Native |
| 4G LTE Cellular | Yes (OpenWay Riva) | Yes (E360/GRID360) | Yes (cellular module) | Optional |
| Power Quality (IEC 61000) | Optional IQ module | E650 extended PQ | ION9000 Class A | EPM 9450 |
| East Coast Utility Acceptance | Very High (ConEd, Eversource) | Very High (NGrid, PSE&G) | Medium-High (varies) | Medium (transmission focus) |
| Typical Lead Time | 8–16 weeks | 8–16 weeks | 10–20 weeks | 12–20 weeks |
| Indicative Price (MV unit) | $1,500–$4,500 | $1,800–$5,000 | $3,000–$8,000 | $2,000–$6,000 |

# Section 7: Delta Metering Specification Package

This section provides Delta's standard technical specification template for utility revenue metering systems. This template is designed to be adapted on a per-project basis, filled in with site-specific data, and submitted as part of the interconnection application metering package.

## 7.1 Complete Technical Specification Template

### 7.1.1 Project Information Block

| Field | Value / Description |
| --- | --- |
| Project Name | [PROJECT NAME] |
| Delta Project Number | [DELTA-XXXX] |
| Site Address | [SITE ADDRESS] |
| Utility | [UTILITY NAME] |
| Utility Account / Meter Number | [ACCOUNT NO.] |
| System Voltage (Primary) | [kV] |
| Maximum Installed DER Capacity | [kW AC] |
| Maximum Import Demand | [kW] |
| Maximum Export Capacity | [kW] |
| Net Metering Tariff | [TARIFF CODE] |
| Interconnection Application Number | [APP NO.] |
| Metering Configuration | [Primary / Secondary / Self-Contained] |
| Revenue Meter Owner | [Customer / Utility] |
| CT/PT Owner | [Customer / Utility] |
| Metering Engineer | [NAME, PE License No.] |
| Date of This Document | [DATE] |

### 7.1.2 Current Transformer Specification

| CT Parameter | Specified Value |
| --- | --- |
| Manufacturer / Model | [VENDOR / MODEL NO.] |
| Number of Phases | 3 (3-phase, 3-wire or 4-wire per system) |
| Primary Current Rating (IN) | [A] |
| Secondary Current Rating | 5 A |
| CT Ratio | [NNN]:5 |
| Accuracy Class (IEEE C57.13) | [0.15S / 0.3S / 0.3] |
| Rated Burden | [B-0.2 / B-0.5 / B-1.0] |
| Calculated Actual Burden | [Ω] (see burden calculation sheet) |
| Short-Time Thermal Rating | [kA rms for 1 sec] |
| Primary Voltage Insulation Class | [15 kV / 35 kV] |
| Frequency | 60 Hz |
| Ambient Temperature Range | –40°C to +70°C |
| Metering vs. Relaying Core | SEPARATE metering and relaying cores; never combined |
| Mounting | [Outdoor pad-mount / indoor substation] |
| CT IEEE C57.13 Certification | [Certificate No. / Test Report No.] |

### 7.1.3 Potential Transformer (PT/VT) Specification

| PT Parameter | Specified Value |
| --- | --- |
| Manufacturer / Model | [VENDOR / MODEL NO.] |
| Number of Phases | 3 |
| Primary Voltage Rating | [kV] |
| Secondary Voltage Rating | 120 V (standard) |
| PT Ratio | [NNN]:1 |
| Accuracy Class (IEEE C57.13) | 0.3 (metering); 1.2Y (relaying) – separate windings |
| Rated Secondary Burden (VA) | [VA] |
| Calculated Actual Burden (VA) | [VA] (see burden calculation sheet) |
| Primary Voltage Insulation Class | [15 kV / 35 kV] |
| Frequency | 60 Hz |
| Thermal Rating | 200% continuous (for overvoltage events) |
| PT IEEE C57.13 Certification | [Certificate No. / Test Report No.] |

### 7.1.4 Revenue Meter Specification

| Meter Parameter | Specified Value |
| --- | --- |
| Manufacturer / Model | [VENDOR / MODEL] – from utility approved list |
| Meter Form | [Form 9S / 36S / etc. per utility standard] |
| ANSI C12.20 Accuracy Class | Class 0.2 |
| Measurement Type | Bi-directional (import and export) |
| Interval Recording | 15-minute intervals (kWh import, kWh export, kVARh, kW demand) |
| Voltage Input (CT-metered) | 120 V nominal from PT secondary |
| Current Input (CT-metered) | 5 A nominal from CT secondary |
| Communication Module | [ANSI C12.22 / cellular LTE / RF mesh] per utility AMI program |
| Optical Port | ANSI C12.18 compliant optical port for local programming |
| DNP3 Support | [Yes / No / Module required] – verify with utility metering engineering |
| Display | LCD with backlight; 6-digit kWh register; rolling demand display |
| Data Security | Password-protected configuration; tamper event logging |
| Environmental Rating | NEMA 4X enclosure (outdoor installations) |
| UL Listing | UL Listed; ANSI C12.1 performance certified |

## 7.2 Installation Requirements

Metering Enclosure: NEMA 4X rated; stainless steel or fiberglass preferred for coastal environments. Secure with utility-specified lock (e.g., PSE&G hex lock, ConEd bolt seal).

Mounting Height: Meter center between 4 ft 6 in. and 5 ft 6 in. above finished grade (ConEd, Eversource standard). Verify with each utility.

Clearance: Minimum 4 ft wide by 3 ft deep clear working space in front of meter enclosure (NEC 110.26 and utility standard).

Conduit: Dedicated PVC or rigid metallic conduit for metering secondary wiring. No other wiring in metering conduit. Sealtite conduit for flexible final connections.

Wiring: #10 AWG stranded copper minimum; continuous without splices; color-coded per ANSI standard (Phase A = Black, Phase B = Red, Phase C = Blue, Neutral = White, Ground = Green).

Shorting Blocks: Install shorting terminal blocks (e.g., Weidmüller or Entrelec) on all CT secondary circuits to allow safe meter maintenance without de-energizing the primary.

CT Circuit Labeling: Clearly label all CT secondary terminals with phase identification (A1, A2, B1, B2, C1, C2) and CT ratio.

Sealing: After final utility acceptance and programming, utility seals CT/PT terminals and meter socket. Do not break seals without contacting utility.

Grounding: Dedicated single-point ground bond for CT/PT secondary neutral. Use separate #6 AWG green ground conductor to dedicated grounding electrode.

CT Cabinet: CT/PT cabinet separate from meter cabinet; minimum 36" separation if in same enclosure. Label "METERING – UTILITY ACCESS REQUIRED".

## 7.3 Testing and Commissioning Procedures

### 7.3.1 Pre-Energization Tests

Visual Inspection: Verify CT/PT model, ratio, accuracy class, and IEEE C57.13 certificate against specification sheet.

Polarity Verification: Confirm H1/X1 polarity per utility specification (Eversource: H1 white dot faces line side). Use polarity indicator or clamp-on millivoltmeter before energization.

CT Shorting: Confirm all CT secondary circuits are shorted at shorting terminal blocks before energizing primary.

Wiring Check: Trace and verify all secondary wiring connections against approved metering one-line diagram.

Insulation Test: Megger test CT/PT secondary wiring at 500 V DC; record insulation resistance (must be >10 MΩ).

Burden Measurement: Measure CT and PT secondary circuit impedance with RLC meter; compare to burden calculation; must not exceed rated burden.

### 7.3.2 Energized Commissioning Tests

CT Ratio Verification: Use clip-on current probe on primary and measure 5 A secondary; calculate ratio; compare to nameplate. Repeat for all three phases.

PT Ratio Verification: Measure PT primary voltage with approved HV voltmeter; measure secondary; calculate ratio; compare to nameplate.

Phase Rotation Check: Use phase rotation meter on meter terminals; confirm ABC (forward) rotation. Incorrect rotation causes meter to measure reactive power incorrectly.

Power Factor Check: Compare EMS-measured power factor to meter display; must agree within ±0.01.

Watt-Hour Test: Operate known load for a defined period; compare meter register increment to calculated energy (P × t). Accuracy ±0.5% required.

Communication Test: Verify DNP3/ANSI C12.22 data transmission to utility AMI head-end; confirm all mapped data points are received with correct scaling and sign convention.

Remote Read Test: Utility metering engineer confirms meter data is received in their billing system; sign-off on commissioning form.

Seal Application: Utility seals CT/PT terminal blocks and meter socket after successful commissioning. Record seal numbers in commissioning record.

## 7.4 Quality Assurance Requirements

Drawing Review: Metering one-line diagram reviewed and stamped by a licensed Professional Engineer (PE) before submission to utility.

Utility Pre-Approval: All metering drawings and specifications submitted to and approved by utility metering engineering before installation begins.

Procurement Verification: CT/PT IEEE C57.13 test reports and meter ANSI C12.20 calibration certificates obtained from vendor at time of procurement and filed in project documentation.

Installation Inspection: Delta QA inspector performs pre-energization walkthrough against Delta Standard Metering Checklist before requesting utility commissioning test.

Commissioning Witness: Utility metering engineer witnesses all energized commissioning tests. Schedule 2–4 weeks in advance.

As-Built Drawings: Metering one-line and conduit/wiring drawings updated to as-built status within 30 days of commissioning.

Records Retention: All metering test records, certificates, and as-built drawings retained for minimum 7 years (or as required by utility agreement, whichever is longer).

# Section 8: Revenue-Leakage Prevention Checklist

Revenue leakage in metering systems refers to systematic errors that cause the recorded energy measurement to differ from the actual energy flow, resulting in financial losses to either the customer or the utility. For Delta's microgrid projects, revenue leakage has four primary consequences: (1) under-billing of DER generation credits, (2) over-billing of demand charges, (3) failed utility commissioning inspection requiring costly re-work, and (4) potential clawback of revenue credits after a metering audit. The following checklist organizes prevention strategies across the project lifecycle.

## 8.1 Common Revenue Leakage Points

| Leakage Source | Description | Financial Impact | Detection Method |
| --- | --- | --- | --- |
| CT Polarity Reversal | H1/H2 terminals reversed on one or more phases; power measured as negative when should be positive (or vice versa) | Export credits not received; import charges applied to export energy | Power factor sign; watt-hour test; phase angle measurement |
| Wrong CT Ratio | CT ratio on meter programmed incorrectly (e.g., 400:5 programmed as 200:5) | All energy readings doubled or halved; systematic 100% error | Ratio test; compare meter read to EMS check meter |
| CT Secondary Open Circuit | Loose terminal, blown fuse (never use), or broken wire in CT circuit; CT saturates | Zero or erratic current measurement; missed energy; potential hazard | Voltage measurement on open terminal; visual inspection |
| Excess CT Burden | CT secondary circuit impedance exceeds rated burden; CT ratio error increases | Systematic under-measurement of current; missed energy | Burden measurement with RLC meter; compare to CT burden rating |
| PT Ratio Error | PT secondary voltage incorrect due to wrong ratio or tap selection | All energy proportional to voltage error (voltage²) | PT ratio test; compare to system voltage |
| Phase-to-Phase Wiring Error | Phase A current wired to Phase B voltage input (and/or vice versa) | Power factor and power measured incorrectly; demand charges incorrect | Phase rotation test; phasor diagram analysis |
| Multiple CT Secondary Grounds | CT secondary neutral grounded at multiple points; stray currents induced | Low-level continuous error; intermittent voltage measurement errors | Ground resistance measurement at each ground point |
| Meter Programming Error | CT ratio, PT ratio, or multiplier programmed incorrectly in meter firmware | Systematic proportional error in all measurements | Read meter registers with optical probe; verify CT/PT multipliers |
| Communication Outage | AMI modem offline; utility does not receive interval data; utility estimates billing | Estimated billing may be inaccurate; lost export credit documentation | Monitor AMI communication status; redundant SIM cards |
| Demand Register Mis-programming | 15-min demand interval set to 30-min or 60-min; peak demand recorded higher | Higher demand charges billed; loss of demand credit accuracy | Verify demand interval in meter register read |
| Reactive Power Sign Error | VAR measurement sign inverted; power factor reported incorrectly | Power factor penalty charges may apply incorrectly | Compare meter PF to EMS PF; phasor analysis |
| Missing Bi-directional Registration | Meter programmed for uni-directional only; export energy not recorded | 100% loss of net metering credit for all exported energy | Verify meter registers for import and export channels |

## 8.2 Prevention Strategies by Project Phase

### 8.2.1 Design Phase

☐ Verify CT/PT specifications against utility metering manual for the specific territory (ConEd, Eversource, PSE&G, etc.).

☐ Perform and document burden calculations; confirm total burden < CT rated burden with minimum 20% safety margin.

☐ Specify 0.3S or 0.15S accuracy class for all renewable and bidirectional DER applications.

☐ Specify separate metering and relaying cores; document in spec that metering CTs are not shared with protection relays.

☐ Confirm CT/PT ratios with utility metering engineering before finalizing drawings.

☐ Specify bi-directional meter with both import and export registers.

☐ Specify correct meter form factor for the utility's metering socket standard.

☐ Include demand interval (15-minute) in meter specification; confirm with utility.

☐ Obtain utility approval of metering one-line drawing before issuing for construction.

### 8.2.2 Procurement Phase

☐ Obtain IEEE C57.13 test reports for all CTs and PTs; verify accuracy class and burden rating match specification.

☐ Obtain ANSI C12.20 calibration certificate for the revenue meter.

☐ Confirm meter model is on utility approved meter list for this specific territory.

☐ Confirm correct communication module is included (ANSI C12.22 / cellular LTE per utility AMI program).

☐ Confirm CT/PT ratios on equipment nameplates match approved drawings before shipping to site.

### 8.2.3 Installation Phase

☐ Verify CT polarity (H1 faces line/utility side) during installation; do not rely on conduit routing for polarity determination.

☐ Maintain CT secondary circuit continuity at all times; install shorting blocks before disconnecting any CT circuit.

☐ Install single-point ground on CT secondary neutral; verify no additional grounds exist.

☐ Verify wiring color-code; trace each conductor from CT to meter terminal before energizing.

☐ Install dedicated metering conduit; verify no non-metering conductors in conduit.

☐ Measure secondary circuit impedance (burden) with RLC meter before energizing; record results.

☐ Perform 500 V DC megger test on all CT/PT secondary wiring; record results (must be >10 MΩ).

### 8.2.4 Commissioning Phase

☐ Perform ratio test on all CTs and PTs under load; compare to nameplate ratios; document results.

☐ Perform phase rotation test at meter terminals; confirm forward (ABC) rotation.

☐ Compare meter power reading to EMS/SCADA power reading; difference must be <1%.

☐ Verify meter register programming: CT ratio, PT ratio, demand interval (15 min), bi-directional registration.

☐ Perform watt-hour test with known load; verify accuracy within ±0.5%.

☐ Verify communication link to utility AMI; confirm all data points received and scaled correctly.

☐ Obtain utility metering engineer sign-off; document seal numbers applied by utility.

### 8.2.5 Operations and Maintenance Phase

☐ Compare utility bill energy totals to EMS/SCADA recorded energy monthly; investigate any discrepancy >1%.

☐ Monitor AMI communication link status daily; alert on extended communication outage (>4 hours).

☐ Verify metering seals are intact during annual site inspections; report any broken seals to utility immediately.

☐ Do not perform maintenance on CT circuits without shorting terminal blocks closed and written utility work permit.

☐ Schedule utility re-test of metering at 5-year intervals (or per utility meter testing program schedule).

☐ Document any meter replacements, firmware updates, or register resets with date, personnel, and utility notification.

## 8.3 Verification Procedures

The following periodic verification procedures are recommended to detect revenue leakage during ongoing project operations:

| Verification Check | Frequency | Method | Pass Criterion | Action if Fail |
| --- | --- | --- | --- | --- |
| Bill vs. EMS energy comparison | Monthly | Compare utility bill kWh import/export to EMS 15-min interval sum | Discrepancy <1.0% | Investigate immediately; notify utility if >2% |
| AMI communication status | Daily (automated) | Monitor AMI head-end for data gaps | No gaps >15 min | Replace SIM; check modem; notify utility |
| Demand charge review | Monthly | Compare utility billed demand to EMS recorded 15-min peak | Within 2% | Audit meter demand interval programming |
| Power factor review | Monthly | Compare utility billed PF to EMS average PF | Within 0.02 PF | Check VAR sign convention; re-test phasor |
| Physical metering inspection | Annual | Visual inspection of seals, wiring, enclosure | All seals intact; no physical damage | Contact utility; schedule re-test |
| CT burden re-measurement | Every 5 years | De-energize, measure CT circuit impedance | Below rated burden | Replace aging wiring or terminals |
| Ratio accuracy re-test | Every 5 years | Utility meter test under load | Within accuracy class tolerance | Replace CT/PT or meter as required |

# References

[1] IEEE Std 2030.7-2017, Standard for the Specification of Microgrid Controllers.

[2] IEEE Std 2030.8-2018, Standard for the Testing of Microgrid Controllers.

[3] ANSI C12.1, Code for Electricity Metering.

[4] ANSI C12.20, American National Standard for Electricity Meters – 0.2 and 0.5 Accuracy Classes.

[5] IEEE C57.13, Requirements for Instrument Transformers.

[6] IEC 61869, Instrument Transformers (all parts).

[7] IEC 62056 (DLMS/COSEM), Electricity metering data exchange.

[8] Con Edison, Electric Service Reference Manual ("Blue Book"), Section VII. www.coned.com.

[9] Con Edison, MES-350, HT Metering Specification. www.coned.com.

[10] Eversource, Requirements for Electric Service ("Yellow Book"), NB-3. www.eversource.com.

[11] Eversource, Rules and Regulations for Electric Service. www.eversource.com.

[12] PSE&G, Transmission Interconnection Requirements, Document 063436. www.pseg.com.

[13] NJ BPU, Net Metering Rules and Regulations. www.energysage.com/local-data/net-metering/pseg.

[14] Dominion Energy, Interconnection Parameters for Distributed Energy Resources Manual. www.dominionenergy.com.

[15] Dominion Energy, Facility Interconnection Requirements. www.dominionenergy.com.

[16] National Grid, Engineering Standard ESB 756. www.nationalgridus.com.

[17] National Grid, MA M.D.P.U. No. 1468 DG Interconnection Tariff. www.nationalgridus.com.

[18] NY PSC, Standardized Interconnection Requirements (SIR). dps.ny.gov.

[19] NY PSC, Default IEEE 1547-2018 Setting Requirements. dps.ny.gov.

[20] ISO-NE, 2018 Source Requirements Document (SRD). iso-ne.com.

[21] PJM, Manual 14G, Generation Interconnection Requests. pjm.com.

[22] PJM, Manual 07, Protection Standards. pjm.com.

[23] BPA, Metering Application Guide for Instrument Transformers. bpa.gov.

[24] NEMA, ANSI C12 / IEC 62056 Standards Overview. nema.org.

[25] Duke Energy, Integrated System and Operations Planning (ISOP) Framework. duke-energy.com.

[26] Delta Engineering, IEEE 2030.7/2030.8 Microgrid Compliance Report for East Coast Utility Jurisdictions, June 2026 (Internal Report).

[27] IEEE 1547-2018, Standard for Interconnection and Interoperability of DER with Associated Electric Power Systems.

[28] UL 1741, Standard for Inverters, Converters, Controllers and Interconnection System Equipment for Use With Distributed Energy Resources.

[29] NERC CIP Standards (CIP-002 through CIP-014), Critical Infrastructure Protection.

[30] Sunspec Alliance, Sunspec Modbus Register Map for Inverters and Meters. sunspec.org.