# What the Existing PCS3440 Model Already Does

From the PSCAD schematic (PCS3440.pdf) and the generated EMTDC Fortran (BESS_1_1Dyn / BESS_1_1Out), the PCS3440 + DELTerr Mi2 BESS module is a selfcontained, closed-loop converter. The external interface is intentionally small:

- PQref(1) = Pref — active power setpoint (kW)

- PQref(2) = Qref1 — reactive power setpoint (kVAR)

- SetupWord / CommandWord — assembled from sliders VRT_Enable, PROT_Enable, HPF_Enable, AVR, FW_EN

- MCB_DRV1 / MCB_DRV2 — AC breaker drive (Timed Breaker, Open@t0)

- AuxCtrl sliders: RampRate, LVRT_ENTER, HVRT_ENTER, Kfactor_VRT, VgridHpf_F

- AVR Q-V curve points: VQ_V1..V4, VQ_Q1..Q4

- V/F trip thresholds and times pre-loaded as constants (OVP1..4, UVP1..4, OFP1..3, UFP1..5 + *Timems)

Outputs available to tap into:

- P, Q, I_active, I_reactive (from internal FFT_Mod)

- Vlrms (Vab, Vbc, Vca RMS)

- Bat_SOC, Ibat1, BatVolt

- PCS Fault, DebugData1, DebugData2

- MCB, MC, DC_EN, DC_SS_EN, AC_SS_EN, PWM status

Conclusion: the PCS handles its own current loop, PWM (PWM_3Level), OC/SPOV protection, ride-through, and Q-V droop. You do NOT build any inner control. You drive PQref and coordinate the microgrid around it.

Default AuxCtrl Slider Values (from the PSCAD model):

| Slider | Range | Default | Units |
| --- | --- | --- | --- |
| RampRate | 10–1000 | 10 | ms |
| LVRT_ENTER | 0–1000 | 880 | 0.1% |
| HVRT_ENTER | 1000–1200 | 1100 | 0.1% |
| Kfactor_VRT | 0–6 | 2 | — |
| VgridHpf_F | 1–300 | 100 | Hz |
| VRT_Enable / PROT_Enable / HPF_Enable | 0/1 | 1 | — |
| AVR / FW_EN | 0/1 | 0 | — |

Default Q-V Curve (AVR mode):

| Point | V (0.1%) | Q (0.1%) |
| --- | --- | --- |
| 1 | 970 | +312 |
| 2 | 990 | 0 |
| 3 | 1010 | 0 |
| 4 | 1030 | -312 |

Hardware confirmed in the model: 20 parallel modules (scaler s=20.0), 690 V LV bus, LCL filter 0.010 mH + 20 µF + 0.010 mH + 0.2 mH per phase, DC bus 5.0 mF + 1.0 Ω pre-charge gated by DCC_SS_EN1. Per-PCS rated ~5 MW (250 kW/module × 20).

# Control Architecture to Build (Above the PCS Block)

Three layers on top of the existing PCS/BESS block — each a separate PSCAD page so it can be tested independently.

## Layer A — Unit Controller (one per PCS+BESS pair)

- Inputs from PCS: P, Q, Bat_SOC, BatVolt, PCS Fault, MCB status, Vlrms.

- Inputs from MGC: P_cmd, Q_cmd, mode flag (PQ vs. grid-forming), enable.

- Outputs to PCS: PQref(1)=Pref, PQref(2)=Qref1, plus SetupWord/CommandWord bit assembly.

- Logic: ramp-rate limiter, SOC clamp (charge blocked >95%, discharge blocked <10%), fault latch, mode switch.

- Grid-forming mode: set AVR=1; feed VQ_V1..V4/VQ_Q1..Q4 droop; PCS handles the rest.

## Layer B — Microgrid Controller (MGC)

- Inputs: both Unit Controllers, GT (P,f,V), utility breaker, building load, 13.2 kV bus V/f.

- Outputs: P_cmd, Q_cmd, mode flag to each Unit Controller; GT start/stop; utility breaker.

- Power-sharing: P_PCS1 = P_total × SOC1/(SOC1+SOC2), P_PCS2 = P_total − P_PCS1.

- State machine: GRID_TIED → ISLAND_DETECT → ISLAND → RESYNC → RECONNECT.

- Black-start: GT start → bus energize → PCS in grid-following → close priority loads.

- Load shedding: trip lowest-priority load if f<59.5 Hz or SOC<20%.

- Anti-islanding: explicitly listed as 'TBD' in the model — build it here.

## Layer C — SCADA / EMS Dispatch Emulator

- Lookup table: time vs. P_dispatch, Q_dispatch driving the MGC.

- Peak-shaving: if building_P > threshold, discharge BESS to cap import.

- TOU: charge off-peak, discharge on-peak.

- All commands feed MGC, not the PCS directly.

# Signal Interface to the Existing PCS Block

Exact signals to tap into BESS_1_1. Do NOT edit internal Fortran — only wire to labeled ports.

| PCS Port / Slider | Direction | Drive From | Notes |
| --- | --- | --- | --- |
| PQref(1) — Pref | Input | Unit Controller | Active power setpoint, kW |
| PQref(2) — Qref1 | Input | Unit Controller | Reactive setpoint, kVAR |
| VRT_Enable | Input slider | Unit Controller | 1 = enable LVRT/HVRT |
| PROT_Enable | Input slider | Unit Controller | 1 = enable V/F trips |
| AVR | Input slider | Unit Controller | 1 = enable Q-V droop curve |
| FW_EN | Input slider | Unit Controller | 1 = enable freq-watt |
| HPF_Enable | Input slider | Unit Controller | 1 = enable HPF on Vgrid |
| RampRate | Input slider | Unit Controller | ms ramp |
| LVRT_ENTER / HVRT_ENTER | Input slider | Site config | 0.1% steps |
| VQ_V1..V4, VQ_Q1..Q4 | Input slider | Unit Controller | Q-V droop curve |
| MCB_DRV1 / MCB_DRV2 | Input | MGC | AC breaker drive |
| P, Q | Output | MGC, EMS | Measured P/Q |
| Vlrms (3-phase) | Output | MGC | Grid voltage RMS |
| Bat_SOC | Output | Unit Controller, EMS | Battery SOC % |
| PCS Fault | Output | Unit Controller, MGC | Fault bitmask |
| MCB, MC, DC_EN, DC_SS_EN, AC_SS_EN | Output | MGC | Breaker/contactor status |

# Task List

## Task 1 — Wrap the Existing PCS+BESS Block as a Reusable Subsystem

Objective: Make BESS_1_1 callable as a clean black box with a defined port list.

Steps:

- Create PSCAD page PCS_Unit_1; drop in existing BESS_1_1.

- Expose external ports: P_cmd, Q_cmd, mode, enable (in); P_meas, Q_meas, SOC, V_rms, Fault, MCB_status (out).

- Wire P_cmd/Q_cmd to PQref via Scalar/Array Tap (PQref(1)=Pref, PQref(2)=Qref1).

- Mirror VRT_Enable, PROT_Enable, AVR, FW_EN, HPF_Enable as external slider inputs.

- Duplicate as PCS_Unit_2.

Deliverable: Two PCS_Unit subsystems with identical port interfaces. Task 2 — Build the Unit Controller Block

Objective: Create the lowest-level controller between MGC and PCS_Unit.

Steps:

- Page Unit_Controller: in (P_cmd, Q_cmd, mode, SOC, Fault); out (P_ref, Q_ref).

- Ramp-rate limiter before passing P_cmd to PCS.

- SOC clamp: charge blocked at SOC>95%; discharge blocked at SOC<10%.

- Fault latch: PCS Fault != 0 → force P_ref=Q_ref=0, raise Unit_Fault.

- Mode switch: 0=PQ; 1=grid-forming (set AVR=1, load Q-V droop).

Deliverable: Unit Controller with step response < 100 ms.

## Task 3 — Build the Microgrid Controller (MGC)

Objective: Coordinate two PCS units, gas turbine, utility breaker.

Steps:

- Page MGC: ingest P_meas/Q_meas/SOC, GT P/V/f, building load, utility status, EMS commands.

- Power-sharing by SOC weighting.

- State machine: GRID_TIED, ISLAND_DETECT, ISLAND, RESYNC, RECONNECT.

- Black-start sequencer: GT → bus → PCS → loads.

- Load shedding on f<59.5 Hz or SOC<20%.

- Add anti-islanding detection (flagged TBD in PCS model).

Deliverable: MGC demonstrates all four mode transitions.

## Task 4 — Build SCADA/EMS Dispatch Emulator

Objective: Provide setpoints to MGC mimicking real EMS dispatch.

Steps:

- Page EMS: lookup table (24-hr compressed) for P_dispatch / Q_dispatch.

- Peak-shaving: if building_P > 4 MW, discharge to cap import.

- TOU rule: off-peak charge / on-peak discharge.

- Feed MGC, not PCS directly.

Deliverable: EMS drives MGC through a representative 24-hr cycle.

## Task 5 — Wire the Gas Turbine and AC Side

Objective: Add missing AC-side so closed loop runs.

Steps:

- 13.2 kV bus, utility Thevenin, utility breaker, building load, step-up xfmrs for each PCS.

- 300 kW sync machine + GAST governor + simple AVR via its own step-up xfmr.

- Bus V/f, line currents, breaker status all wired to MGC.

Deliverable: Full case runs grid-tied at rated power.

## Task 6 — Validation Scenarios

Objective: Prove the control works under realistic disturbances.

Steps:

- S1: P_cmd step 0 → 5 MW → 0. Verify ramp limiter.

- S2: Trip utility; island transition, freq ±0.5 Hz.

- S3: 3-phase fault at 13.2 kV bus; VRT=1, PCS stays connected per IEEE 1547 Cat II.

- S4: Black start from dead bus.

- S5: Resync and reconnect.

- S6: SOC limit — discharge stops at 10%.

Deliverable: Test report with annotated waveforms for each scenario.

# Rules of Engagement (Do Not Break the Existing Model)

- Do NOT edit BESS_1_1Dyn.f / BESS_1_1Out.f — they are auto-generated and will be overwritten.

- Do NOT touch FFT_Mod, PWM_3Level, oc_spov, special_funcs — validated internal blocks.

- Interact only through labeled ports and AuxCtrl sliders.

- SetupWord/CommandWord are opaque — set them via slider switches, not by writing the integer.

- Test in average mode (PROT_Enable=0, VRT_Enable=0) before enabling protections.